## Sheet
________ Preliminary Utility Schedule
September 24, 2024
NO | QTY | DESCRIPTION | VOLTS | PH | AMPS | CW (mm) | HW (mm) | LPH | IW (mm) | DW (mm) | GAS kW | EXH (M^3/H) | EXH S.P. (Pa) | SUPPLY (M^3/H) | SUPPLY S.P. (Pa) | HEAT REJECTION Watts | CHILLED WATER IN | CHILLED WATER OUT | REMARKS
BULK STORAGE AREA
1 | 1 | INSECT CONTROL | 230 | 1 | 0.4 | [13 empty] | WALL MOUNT
2 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
3 | 4 | LIQUOR STORAGE SHELVING | [16 empty] | FIXED FIVE TIER
4 | 1 | LIQUOR COLD ROOM | 230 | 1 | 10 | [13 empty] | WITH RAMP
5 | - | SPARE NUMBER
6 | - | SPARE NUMBER
7 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
8 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
9 | - | SPARE NUMBER
10 | - | SPARE NUMBER
11 | 3 | LIQUOR STORAGE SHELVING | [16 empty] | FIXED FIVE TIER
12 | 2 | WINE STORAGE SHELVING | [16 empty] | FIXED FOURTEEN TIER 186 BOTTLES
13 | 1 | REACH-IN ULTRA LOW TEMP FREEZER | 230 | 1 | 6.5 | [13 empty] | -40°C MOBILE
14 | 1 | HOLDING FREEZER | 230 | 1 | 10 | [13 empty] | WITH RAMP
15 | - | SPARE NUMBER
16 | - | SPARE NUMBER
17 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
18 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
19 | - | SPARE NUMBER
20 | - | SPARE NUMBER
21 | 8 | DAY FREEZER STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
22 | 1 | REACH-IN ULTRA LOW TEMP FREEZER | 230 | 1 | 6.5 | [13 empty] | -40°C MOBILE
23 | 4 | DRY STORAGE SHELVING | [16 empty] | FIXED FIVE TIER
24 | 1 | DUNNAGE RACK
25 | - | SPARE NUMBER
26 | 1 | HIGH-DENSITY SHELVING
27 | 1 | DUNNAGE RACK
28 | 1 | HIGH-DENSITY SHELVING
29 | - | SPARE NUMBER
30 | - | SPARE NUMBER
31 | 1 | KEG COOLER | 230 | 1 | 10 | [13 empty] | WITH RAMP
32 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
33 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
34 | 3 | KEG RACK | [16 empty] | DOUBLE DECK
35 | - | SPARE NUMBER
36 | 1 | BEER SYSTEM | 230 | 1 | 8.6 | [11 empty] | 10 | 10 | WATER COOLED
37 | 1 | KEG LIFTER | 230 | 1 | 8 | [13 empty] | MOBILE
38 | 2 | UTILITY RACK | [16 empty] | MOBILE
39 | - | SPARE NUMBER
40 | - | SPARE NUMBER
41 | 1 | DUMBWAITER | [16 empty] | BY GENERAL CONTRACTOR
42 | 1 | SHELVING UNIT | [16 empty] | FIXED TWO TIER
43 | 1 | MOP SINK | [7 empty] | 50 | [8 empty] | BY GENERAL CONTRACTOR
44 | 1 | HOSE BIBB |  |  |  | 15 | 15 | [11 empty] | BY GENERAL CONTRACTOR
45 | - | SPARE NUMBER
46 | 1 | WALL SHELF | [16 empty] | CUSTOM FABRICATION
47 | 1 | MOP RACK | [16 empty] | BY GENERAL CONTRACTOR
48 | - | SPARE NUMBER
49 | - | SPARE NUMBER
50 | - | SPARE NUMBER
OFFICE AREA
51 | 1 | WORK SURFACE | 230 | 1 | 20 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
52 | 1 | CHAIR | [16 empty] | BY OS&E
53 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
54 | 1 | WALL CABINET | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
55 | - | SPARE NUMBER
56 | - | SPARE NUMBER
57 | 1 | WORK SURFACE | 230 | 1 | 20 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
58 | 1 | CHAIR | [16 empty] | BY OS&E
59 | - | SPARE NUMBER
60 | - | SPARE NUMBER
61 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
62 | 1 | WALL CABINET | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
63 | 1 | WORK SURFACE | 120 | 1 | 20 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
64 | 1 | CHAIR | [16 empty] | BY OS&E
65 | - | SPARE NUMBER
66 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
67 | 1 | WALL CABINET | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
68 | 1 | CHAIR | [16 empty] | BY OS&E
69 | - | SPARE NUMBER
70 | - | SPARE NUMBER
71 | - | SPARE NUMBER
72 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
73 | 1 | WORK SURFACE | 120 | 1 | 20 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
74 | 1 | WALL CABINET | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
75 | - | SPARE NUMBER
76 | 1 | CHAIR | [16 empty] | BY OS&E
77 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
78 | 1 | CHAIR | [16 empty] | BY OS&E
79 | - | SPARE NUMBER
80 | - | SPARE NUMBER
81 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
82 | 1 | CHAIR | [16 empty] | BY OS&E
83 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
84 | 1 | CHAIR | [16 empty] | BY OS&E
85 | - | SPARE NUMBER
86 | 1 | COMPUTER | 230 | 1 | 10 | [13 empty] | BY OS&E
87 | 1 | PRINTER / FAX MACHINE | 230 | 1 | 10 | [13 empty] | BY OS&E
88 | - | SPARE NUMBER
89 | - | SPARE NUMBER
90- 100 | - | SPARE NUMBER
DAY STORAGE AREA
101 | 1 | INSECT CONTROL | 230 | 1 | 0.4 | [13 empty] | WALL MOUNT
102 | 1 | DAY FREEZER | 230 | 1 | 10 | [13 empty] | WITH RAMP
103 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
104 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
105 | - | SPARE NUMBER
106 | 5 | DAY FREEZER STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
107 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
108 | 5 | DRY STORAGE SHELVING | [16 empty] | FIXED FIVE TIER
109 | - | SPARE NUMBER
110- 120 | - | SPARE NUMBERS
MEAT PREPARATION AREA
121 | 1 | SLICER CART | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION MOBILE
122 | 1 | FOOD SLICER | 230 | 1 | 13
123 | 1 | KNIFE SANITIZER | 230 | 1 | 0.3 | [13 empty] | WALL MOUNTED
124 | 1 | MEAT PREPARATION TABLE WITH SINK | 230 | 1 | 10 | 15 | 15 |  | 50 | [9 empty] | CUSTOM FABRICATION
125 | - | SPARE NUMBER
126 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
127 | 1 | MEAT GRINDER | 230 | 1 | 4.2
128 | 1 | VACUUM PACKAGING MACHINE | 230 | 1 | 10 | [13 empty] | MOBILE WITH CUSTOM FABRICATED CART
129 | - | SPARE NUMBER
130 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
131 | 1 | AIR PURIFIER | 230 | 1 | 0.2 | [13 empty] | WALL MOUNTED
132 | 2 | UNDER COUNTER UTILITY RACK | [16 empty] | MOBILE
133 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #167
134 | 1 | PORTION SCALE | 230 | 1 | 2
135 | - | SPARE NUMBER
136 | 1 | EVAPORATOR COIL | 230 | 1 | 1.5 |  |  |  | 20 | [9 empty] | WATER COOLED
137 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
138 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
139 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 4 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER FOR ITEM #136
140 | - | SPARE NUMBER
141 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
142 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
143 | - | SPARE NUMBER
144 | - | SPARE NUMBER
145 | - | SPARE NUMBER
146 | - | SPARE NUMBER
147 | - | SPARE NUMBER
148 | - | SPARE NUMBER
149 | - | SPARE NUMBER
150 | - | SPARE NUMBER
151 | 1 | MEAT COLD ROOM | 230 | 1 | 10 | [13 empty] | WITH RAMP
152 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
153 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
154 | 5 | MEAT COLD STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
155- 160 | - | SPARE NUMBERS
FISH PREPARATION AREA
161 | - | SPARE NUMBER
162 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
163 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
164 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
167 | 1 | FISH PREPARATION TABLE WITH MIXER RECESS | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION
168 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
169 | - | SPARE NUMBER
170 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
171 | 1 | FISH SINK WITH RECESSED CUTTING BOARD | [6 empty] | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #167
172 | 1 | PRE-RINSE UNIT |  |  |  | 15 | 15 | 190 | [10 empty] | WITH FAUCET
173 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
174 | 1 | AIR PURIFIER | 230 | 1 | 0.2 | [13 empty] | WALL MOUNTED
175 | - | SPARE NUMBER
176 | 1 | FOOD PROCESSOR | 230 | 1 | 7
177 | 1 | EVAPORATOR COIL | 230 | 1 | 1.5 |  |  |  | 20 | [9 empty] | WATER COOLED
178 | 1 | VACUUM PACKAGING MACHINE | 230 | 1 | 10 | [13 empty] | MOBILE WITH CUSTOM FABRICATED CART
179 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 4 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER FOR ITEM #177
180 | - | SPARE NUMBER
181 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #167
182 | 2 | PORTION SCALE | 230 | 1 | 2
183 | 2 | UNDER COUNTER UTILITY RACK | [16 empty] | MOBILE
184 | 1 | KNIFE SANITIZER | 230 | 1 | 0.3 | [13 empty] | WALL MOUNTED
185 | - | SPARE NUMBER
186 | 1 | PLANETARY MIXER | 230 | 1 | 3.3 | [13 empty] | 10 LITER
187 | 1 | MIXER UTENSIL RACK | [16 empty] | CUSTOM FABRICATION
188 | - | SPARE NUMBER
189 | - | SPARE NUMBER
190- 195 | - | SPARE NUMBERS
196 | 1 | FISH COLD ROOM | 230 | 1 | 10 | [13 empty] | WITH RAMP
197 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
198 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
199 | - | SPARE NUMBER
200 | - | SPARE NUMBER
201 | 5 | FISH COLD STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
202 | 1 | UTILITY RACK | [16 empty] | MOBILE
203 | 1 | REACH-IN ULTRA LOW TEMP FREEZER | 230 | 1 | 6.5 | [13 empty] | -40°C MOBILE
204 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
205- 220 | - | SPARE NUMBERS
ICE PRODUCTION AREA
221 | 2 | WATER FILTRATION SYSTEM |  |  |  | 20 | [12 empty] | FOR ITEM #222
222 | 2 | ICE MACHINE | 230 | 1 | 6.6 | 15 |  |  | 20 | [6 empty] | 570 | 10 | 15 | 175KG. WATER-COOLED STACKED LARGE CUBE
223 | 1 | ICE BIN | [16 empty] | 454 KG.
224 | 1 | ICE TRANSPORT CART | [16 empty] | 80 KG. MOBILE
225 | - | SPARE NUMBER
226 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
227 | 1 | ICE BIN | [6 empty] | 25 | [9 empty] | 816KG. DIVIDED
228 | 1 | ICE MACHINE | 230 | 1 | 5.2 | 15 |  |  | 20 | [6 empty] | 1200 | 10 | 15 | 600KG. WATER COOLED FLAKE ICE
229 | - | SPARE NUMBER
230 | - | SPARE NUMBER
231 | 2 | ICE TRANSPORT CART | [16 empty] | 114KG. MOBILE
232 | 1 | ICE MACHINE | 230 | 1 | 15.8 | 15 |  |  | 20 | [6 empty] | 1300 | 10 | 15 | 856KG. WATER COOLED CRESCENT ICE
233 | 3 | WATER FILTRATION SYSTEM |  |  |  | 20 | [12 empty] | FOR ITEM #228
234 | 1 | WATER FILTRATION SYSTEM |  |  |  | 20 |  |  | 15 | [9 empty] | FOR ITEM #232
235- 240 | - | SPARE NUMBERS
PRODUCE PREPARATION AREA
241 | 1 | PRODUCE DRYER | 208 | 3 | 3.4 |  |  |  | 50
242 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
243 | 1 | PRODUCE PREPARATION TABLE WITH SINKS AND MIXER RECESS | 230 | 1 | 20 | 15 | 15 | 110 | 50 | [9 empty] | CUSTOM FABRICATION
244 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
245 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
246 | 1 | FOOD PROCESSOR | 230 | 1 | 7
247 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
248 | 1 | VEGETABLE CUTTER | 230 | 1 | 3.7
249 | - | SPARE NUMBER
250 | - | SPARE NUMBER
251 | 1 | VEGETABLE SLICER | 230 | 1 | 3.7
252 | 1 | AIR PURIFIER | 230 | 1 | 0.2 | [13 empty] | WALL MOUNTED
253 | 1 | PLANETARY MIXER | 230 | 1 | 3.3 | [13 empty] | 10 LITER
254 | 1 | MIXER UTENSIL RACK | [16 empty] | CUSTOM FABRICATION
255 | - | SPARE NUMBER
256 | 1 | PRODUCE COLD ROOM | 230 | 1 | 10 | [13 empty] | WITH RAMP
257 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
258 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 6 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER
259 | - | SPARE NUMBER
260 | - | SPARE NUMBER
261 | 9 | PRODUCE COLD STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
262 | 2 | UTILITY RACK | [16 empty] | MOBILE
263 | 1 | KNIFE SANITIZER | 230 | 1 | 0.3 | [13 empty] | WALL MOUNTED
264 | 1 | PRODUCE PREPARATION TABLE | 230 | 1 | 20 | [13 empty] | CUSTOM FABRICATION
265 | - | SPARE NUMBER
266 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION
267 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
268 | 1 | EVAPORATOR COIL | 230 | 1 | 1.5 |  |  |  | 20 | [9 empty] | WATER COOLED
269 | 1 | REFRIGERATION SYSTEM | 230 | 1 | 4 | [11 empty] | 15 | 15 | INDOOR WATER-COOLED WITH EVAPORATOR COIL ON EMERGENCY POWER FOR ITEM #268
270 | - | SPARE NUMBER
271 | - | SPARE NUMBER
272 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
273 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
274 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
275 | - | SPARE NUMBER
276 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
277 | - | SPARE NUMBER
278 | - | SPARE NUMBER
279 | - | SPARE NUMBER
280- 300 | - | SPARE NUMBERS
WAREWASHING AREA
301 | 1 | GLASS WASH TABLE | [16 empty] | CUSTOM FABRICATION
302 | 1 | UNDER COUNTER GLASS WASH MACHINE | 230 | 1 | 14.3 |  | 15 | 140 | 16 | [9 empty] | 89°C RINSE
303 | 1 | GLASS RACK SHELF | [16 empty] | CUSTOM FABRICATION WALL MOUNTED
304 | 1 | UNDER COUNTER GLASS WASH MACHINE | 230 | 1 | 14.3 |  | 15 | 140 | 16 | [9 empty] | 89°C RINSE
305 | - | SPARE NUMBER
306 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
307 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
308 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
309 | - | SPARE NUMBER
310 | - | SPARE NUMBER
311 | 1 | HOSE REEL CONTROL CABINET |  |  |  | 15 | 15 | 95 | [10 empty] | WALL RECESSED FOR ITEM #321
312 | 1 | SOILED DISH TABLE | [16 empty] | CUSTOM FABRICATION WITH TROUGH AND TROUGH COVERS
313 | 1 | FOOD WASTE COLLECTOR | 230 | 1 | 5.5 | 15 | 15 | 55 |  | 50 | [8 empty] | WITH COVER
314 | 1 | PASS-THRU WINDOW AND DROP SHELF | [16 empty] | CUSTOM FABRICATION
315 | - | SPARE NUMBER
316 | 1 | SILVERWARE CHUTE | [16 empty] | CUSTOM FABRICATION
317 | 1 | SILVER SOAK SINK | [16 empty] | MOBILE
318 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
319 | - | SPARE NUMBER
320 | - | SPARE NUMBER
321 | 1 | HOSE REEL | [16 empty] | CEILING MOUNT
322 | 1 | GLASS RACK SHELF | [16 empty] | CUSTOM FABRICATION WALL MOUNTED
323 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
324 | 1 | SILVERWARE CHUTE | [16 empty] | CUSTOM FABRICATION
325 | - | SPARE NUMBER
326 | 1 | SILVER SOAK SINK | [16 empty] | MOBILE
327 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
328 | 1 | CORNER CONVEYOR | [6 empty] | 40
329 | - | SPARE NUMBER
330 | - | SPARE NUMBER
331 | 1 | DISH MACHINE | 400 | 3 | 50 |  | 20 | 120 | 40 | [9 empty] | 89°C RINSE
332 | 1 | CLEAN DISH TABLE | [16 empty] | CUSTOM FABRICATION
333 | 1 | GLASS RACK SHELF | [16 empty] | CUSTOM FABRICATION WALL MOUNTED
334 | 1 | PASS-THRU WINDOW AND SHELF | [16 empty] | CUSTOM FABRICATION
335 | - | SPARE NUMBER
336 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
337 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
338 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
339 | - | SPARE NUMBER
340 | - | SPARE NUMBER
341 | 1 | HOSE REEL CONTROL CABINET |  |  |  | 15 | 15 | 95 | [10 empty] | FOR ITEM #347
342 | 1 | POT SINK |  |  |  | (2)20 | (2)20 | 340 | 50 | [9 empty] | CUSTOM FABRICATION
343 | 1 | POT SHELF | [16 empty] | CUSTOM FABRICATION
344 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
345 | - | SPARE NUMBER
346 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
347 | 1 | HOSE REEL | [16 empty] | CEILING MOUNT
348 | 3 | POT AND PAN DRYING RACK | [16 empty] | MOBILE FIVE TIER
349 | - | SPARE NUMBER
350 | - | SPARE NUMBER
351 | 1 | PLASTIC DOOR
352 | - | SPARE NUMBER
353 | - | SPARE NUMBER
354 | - | SPARE NUMBER
355 | - | SPARE NUMBER
356 | 1 | REVERSE OSMOSIS SYSTEM |  |  |  | 10 |  | 40 | 6 | [9 empty] | FOR ITEM #504 #566
357 | 1 | REVERSE OSMOSIS STORAGE TANK |  |  |  | 10 | [12 empty] | 80 GALLON FOR ITEM #356
358 | - | SPARE NUMBER
359 | - | SPARE NUMBER
360 | - | SPARE NUMBER
361 | 1 | MOP SINK CABINET |  |  |  | 15 | 15 | 15 |  | 50 | [8 empty] | WITH HOSE BIBB
362 | - | SPARE NUMBER
363 | - | SPARE NUMBER
364 | - | SPARE NUMBER
365 | - | SPARE NUMBER
366 | - | SPARE NUMBER
367 | - | SPARE NUMBER
368 | 1 | PLASTIC DOOR
369 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
370 | - | SPARE NUMBER
371 | 1 | GLASS POLISHING TABLE | [16 empty] | CUSTOM FABRICATION
372 | 1 | RACK SHELF | [16 empty] | CUSTOM FABRICATION WALL MOUNTED
373 | 8 | CLEAN DISH STORAGE SHELVING | [16 empty] | FIXED FIVE TIER
374 | - | SPARE NUMBER
375- 400 | - | SPARE NUMBERS
SERVICE BAR AREA
401 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
402 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
403 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
404 | 1 | BEVERAGE COUNTER | [16 empty] | CUSTOM FABRICATION
405 | 1 | BEVERAGE CONDUIT WITH STAINLESS STEEL CHASE
406 | 1 | BEER DISPENSING TOWER | [16 empty] | FOUR TAPS
407 | 1 | DRIP TROUGH WITH GLASS RINSER
408 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
409 | - | SPARE NUMBER
410 | - | SPARE NUMBER
411 | 1 | GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #404
412 | 1 | CO2 TANK | [16 empty] | BY VENDOR
413 | 4 | AIR POT
414 | 2 | AIR POT STAND
415 | - | SPARE NUMBER
416 | 1 | WATER FILTRATION SYSTEM |  |  |  | 20 | [12 empty] | UNDER COUNTER FOR ITEM #413 #414 #423
417 | 1 | COFFEE GRINDER | 230 | 1 | 5.1
418 | 1 | COFFEE AND ICE TEA BREWER | 230 | 1 | 45.5 | 6
419 | - | SPARE NUMBER
420 | - | SPARE NUMBER
421 | 1 | HOT WATER DISPENSER | 230 | 1 | 18.4 | 6
422 | 1 | DOUBLE SAKI WARMER | 230 | 1 | 15
423 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
424 | 2 | COFFEE GRINDER
425 | - | SPARE NUMBER
426 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #404
427 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [16 empty] | CUSTOM FABRICATION
428 | 1 | ESPRESSO MACHINE | 230 | 1 | 26 | 15 |  |  | 25 | [9 empty] | 2 GROUP
429 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
430 | - | SPARE NUMBER
431 | - | SPARE NUMBER
432 | 1 | GLASS FILLER |  |  |  | 15 |  |  | 20 | [9 empty] | WITH DRAIN PAN
433 | 1 | GLASS RINSER |  |  |  | 15 |  |  | 15
434 | 1 | DRY STORAGE SHELVING | [16 empty] | MOBILE FIVE TIER
435 | - | SPARE NUMBER
436 | 1 | RED WINE REFRIGERATOR | 230 | 1 | 1.6 | [13 empty] | MOBILE
437 | 1 | WHITE WINE REFRIGERATOR | 230 | 1 | 1.6
438 | 1 | REACH IN REFRIGERATOR | 230 | 1 | 2.47 | [13 empty] | MOBILE WATER COOLED
439 | - | SPARE NUMBER
440 | - | SPARE NUMBER
441 | 1 | DRINK SERVICE COUNTER | [16 empty] | CUSTOM FABRICATION WITH GLASS RACK
442 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERS PART OF ITEM #441
443 | 1 | REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #434
444 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #442
445 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
446 | 1 | CO2 TANK | [16 empty] | BY VENDOR
447 | 1 | CO2 GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #802
448 | 1 | DROP-IN FREEZER CABINET | 230 | 1 | 1.1
449 | - | SPARE NUMBER
450 | - | SPARE NUMBER
451 | 1 | DIPPERWELL |  |  |  |  | 15 | 20 | 40 | [9 empty] | WITH FAUCET
452 | 1 | PASS-THRU WINDOW AND SHELF | [16 empty] | CUSTOM FABRICATION
453 | 1 | POS SYSTEM | 230 | 1 | 10 | [13 empty] | BY OS&E
454 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
455 | - | SPARE NUMBER
456 | 1 | HOOD CONTROL CABINET | 230 | 1 | 10 | [13 empty] | FOR ITEM #463 #506 #531 #544 #546 #567
457 | - | SPARE NUMBER
458 | - | SPARE NUMBER
459 | - | SPARE NUMBER
460 | - | SPARE NUMBER
BULK PREPARATION AND COOKLINE AREA
461 | 1 | FIRE SUPPRESSION SYSTEM | 230 | 1 | 10 | 25 | [12 empty] | FOR ITEM #463 #506 #531 #544 #546 #567
462 | 1 | SMT RECESSED REMOTE STATION |  |  |  | 10 | 10 | [11 empty] | CONNECT TO ITEM #465
463 | 1 | EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 1801 | 182 | 1081 | 27 |  |  |  | WITH MAKE-UP AIR
464 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
465 | 1 | CENTRAL SANITATION SYSTEM | 230 | 1 | 30 |  | 20 | 1100
466 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
467 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
468 | 1 | FOUR BURNER RANGE | [8 empty] | 44 | [7 empty] | MOBILE
469 | 1 | FILL FAUCET |  |  |  | 20 | 20 | 110
470 | 1 | SALAMANDER | [8 empty] | 10.3 | [7 empty] | WALL MOUNTED
471 | 1 | WORK TABLE | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION
472 | 2 | INGREDIENT BIN | [16 empty] | MOBILE WITH LID
473 | 1 | DOUBLE TUBULAR WALL SHELF | [16 empty] | CUSTOM FABRICATION
474 | 2 | RICE COOKER | [8 empty] | 10.3
475 | 1 | HOSE REEL | [16 empty] | WALL MOUNTED
476 | 2 | RICE WARMER STAND | [16 empty] | CUSTOM FABRICATION MOBILE
477 | 1 | PREPARATION TABLE WITH SINKS | 230 | 1 | 10 | 15 | 15 | 110 | 40 | [9 empty] | CUSTOM FABRICATION WITH SINK COVERS
478 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
479 | - | SPARE NUMBER
480 | - | SPARE NUMBER
481 | 1 | TRASH RECEPTACLE | [16 empty] | WITH LID AND DOLLY
482 | 1 | VEGETABLE DRYER | [16 empty] | MOBILE
483 | 2 | BLENDER | 230 | 1 | 6 | [13 empty] | WITH DOME
484 | 1 | FOOD PROCESSOR | 230 | 1 | 7
485 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
486 | 1 | VEGETABLE JUICER | 230 | 1 | 7
487 | 1 | CITRUS JUICER | 230 | 1 | 2.2
488 | 1 | IMMERSION CIRCULATOR | 230 | 1 | 4.8
489 | - | SPARE NUMBER
490 | - | SPARE NUMBER
491 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
492 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
493 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
494 | 1 | PASTRY PREPARATION COUNTER WITH MIXER RECESS | [16 empty] | CUSTOM FABRICATION
495 | - | SPARE NUMBER
496 | 1 | RECESSED MARBLE TOP | [16 empty] | PART OF ITEM #494
497 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION WITH INGREDIENT BINS
498 | 1 | INDUCTION WARMER | 230 | 1 | 22 | [13 empty] | 2 RING
499 | - | SPARE NUMBER
500 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
501 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOORS PART OF ITEM #491
502 | 1 | 20 LITER MIXER | 230 | 1 | 1.6
503 | 1 | MIXER UTENSIL RACK | [16 empty] | CUSTOM FABRICATION
504 | 1 | COMBI OVEN WITH BLAST CHILLER | 230 | 1 | 4.7 | (2)15 |  |  | 30 40 |  | 14.1 | [7 empty] | MOBILE
504 | 1 | COMBI OVEN WITH BLAST CHILLER | 230 | 1 | 13.9 | (2)15 |  |  | 30 40 | [9 empty] | MOBILE
505 | - | SPARE NUMBER
506 | 1 | EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 1271 | 239 | 763 | 27 |  |  |  | WITH MAKE-UP AIR
507 | - | SPARE NUMBER
508 | - | SPARE NUMBER
509 | - | SPARE NUMBER
510- 530 | - | SPARE NUMBER
FINISH COOKLINE AREA
531 | 1 | EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 14772 | 483 | 4430 | 81 |  |  |  | WITH MAKE-UP AIR
532 | 1 | AUTO GYOZA COOKER
533 | 1 | FREEZER EQUIPMENT STAND | 230 | 1 | 2.5 | [13 empty] | MOBILE WATER COOLED
534 | 1 | SPREADER | [16 empty] | MOBILE
535 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
536 | 1 | TEMPURA FRYER | [8 empty] | 35.6
537 | 1 | PASTA COOKER |  |  |  | 15 |  |  | 25 |  | 23.5 | [7 empty] | MOBILE
538 | 1 | FOUR BURNER RANGE | [8 empty] | 49.8 | [7 empty] | MOBILE WITH CONVECTION OVEN
539 | 1 | FILL FAUCET |  |  |  | 20 | 20 | 110
540 | 1 | SALAMANDER | [8 empty] | 10.3 | [7 empty] | WALL MOUNTED
541 | 1 | TUBULAR WALL SHELF | [16 empty] | CUSTOM FABRICATION
542 | 1 | SIX BURNER RANGE | 230 | 1 | 3 | [5 empty] | 70.3 | [7 empty] | MOBILE WITH CONVECTION OVEN
543 | 1 | SALAMANDER | [8 empty] | 10.3 | [7 empty] | WALL MOUNTED
544 | 1 | EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 14772 | 483 | 4430 | 81 |  |  |  | WITH MAKE-UP AIR
545 | - | SPARE NUMBER
546 | 1 | SOLID FUEL EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 14772 | 483 | 4430 | 81 |  |  |  | WITH MAKE-UP AIR
547 | 1 | FILL FAUCET |  |  |  | 20 | 20 | 110
548 | 1 | CHARCOAL GRILL AND OVEN | [16 empty] | MOBILE
549 | - | SPARE NUMBER
550 | - | SPARE NUMBER
551 | 1 | INDUCTION WARMER | 230 | 1 | 22 | [13 empty] | 2 RING
552 | 1 | INDUCTION WARMER | 230 | 1 | 15 | [13 empty] | 1 RING
553 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
554 | 1 | PASTRY PREPARATION COUNTER | [16 empty] | CUSTOM FABRICATION
555 | - | SPARE NUMBER
556 | 1 | INGREDIENT BIN | [16 empty] | MOBILE WITH LID
557 | 1 | 10L. MIXER | 230 | 1 | 13
558 | 1 | SHAVED ICE MACHINE | 230 | 1 | 0.9
559 | - | SPARE NUMBER
560 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
561 | 1 | DESERT FREEZER | 230 | 1 | 4.1
562 | 1 | UNDERCOUNTER FREEZER | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
563 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
564 | 1 | COUNTERTOP FRYER | 230 | 1 | 24
565 | - | SPARE NUMBER
566 | 1 | COUNTERTOP COMBI OVEN | 230 | 1 | 4.7 | (2) 15 |  |  | 30 |  | 14.1 | [7 empty] | MOBILE
567 | 1 | EXHAUST HOOD | 230 | 1 | 10 | [6 empty] | 14772 | 483 | 4430 | 81 |  |  |  | WITH MAKE-UP AIR
568 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
569 | - | SPARE NUMBER
570- 580 | - | SPARE NUMBERS
CHEF'S COUNTER AREA
581 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH ELECTRIC FAUCET SOAP AND TOWEL DISPENSER
582 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
583 | 1 | UV INSPECTION CABINET | [16 empty] | WALL MOUNTED
584 | 1 | CHEF'S COUNTER WITH SINK | 230 | 1 | 10 | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION
585 | - | SPARE NUMBER
586 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #584
587 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [16 empty] | CUSTOM FABRICATION
588 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #584
589 | - | SPARE NUMBER
590 | - | SPARE NUMBER
591 | 1 | DOUBLE WALL SHELF | [16 empty] | CUSTOM FABRICATION
592 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS AND DRAWERS AND NSF7 RAIL WATER COOLED
594 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
595 | - | SPARE NUMBER
596 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS AND DRAWERS AND NSF7 RAIL WATER COOLED
597 | 1 | CHECK STRIP | [16 empty] | CUSTOM FABRICATION
598 | 1 | PASS-THRU WINDOW AND SHELF | [16 empty] | CUSTOM FABRICATION
599 | - | SPARE NUMBER
600 | 4 | RETRACTABLE FOOD WARMER | 230 | 1 | 1.6
601 | 1 | UNDER SHELF TASK LIGHT | 230 | 1 | 0.2
602 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS AND DRAWERS AND NSF7 RAIL WATER COOLED
603 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #584
604 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [16 empty] | CUSTOM FABRICATION
605 | - | SPARE NUMBER
606 | - | SPARE NUMBER
607 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
608 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 | [13 empty] | CUSTOM FABRICATION WITH DOORS AND DRAWERS AND NSF7 RAIL WATER COOLED
609 | - | SPARE NUMBER
610 | - | SPARE NUMBER
611 | 1 | DIPPERWELL |  |  |  |  | 15 | 20 | 40 | [9 empty] | WITH FAUCET
612 | 1 | DROP-IN FREEZER CABINET | 230 | 1 | 1.1
613 | 1 | RECESSED MARBLE TOP | [16 empty] | CUSTOM FABRICATION PART OF ITEM #584
614 | - | SPARE NUMBER
615- 700 | - | SPARE NUMBERS
SUSHI BAR AREA
701 | 1 | SUSHI BAR BACK COUNTER | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION
702 | 1 | RICE WARMER | 230 | 1 | 0.2
703 | 1 | DIPPERWELL |  |  |  |  | 15 | 20 | 40 | [9 empty] | WITH FAUCET
704 | 1 | DROP-IN HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH SOAP & TOWEL DISPENSER
705 | - | SPARE NUMBER
706 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [16 empty] | CUSTOM FABRICATION
707 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
708 | 1 | SUSHI CASE | 230 | 1 | 5 | [13 empty] | CUSTOM FABRICATION REMOTE REFRIGERATION
709 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
710 | - | SPARE NUMBER
711 | 1 | TOWEL WARMER | 230 | 1 | 1.9
712 | - | SPARE NUMBER
713 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED PART OF ITEM #701
714 | 1 | OPEN INSULATED CABINET | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION PART OF ITEM #701
715 | - | SPARE NUMBER
716 | 1 | TOASTER OVEN | 230 | 1 | 7.2 | [13 empty] | UNDER COUNTER
717 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION WATER COOLED PART OF ITEM #701
718 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
719 | - | SPARE NUMBER
720 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
721 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION PART OF ITEM #701
722 | - | SPARE NUMBER
723 | 1 | SUSHI CASE | 230 | 1 | 5 | [13 empty] | CUSTOM FABRICATION REMOTE REFRIGERATION
724 | 1 | OPEN INSULATED CABINET | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION PART OF ITEM #701
725 | - | SPARE NUMBER
726 | 1 | TOASTER OVEN | 230 | 1 | 7.2 | [13 empty] | UNDER COUNTER
727 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION WATER COOLED PART OF ITEM #701
728 | 1 | OPEN STORAGE CABINET | [16 empty] | CUSTOM FABRICATION PART OF ITEM #701
729 | - | SPARE NUMBER
730 | - | SPARE NUMBER
731 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
732 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [16 empty] | CUSTOM FABRICATION
733 | 1 | DROP-IN HAND SINK |  |  |  | 15 | 15 | 20 |  | 40 | [8 empty] | WITH SOAP & TOWEL DISPENSER
734 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
735- 750 | - | SPARE NUMBERS
751 | 1 | SUSHI FRONT SERVING COUNTER | [16 empty] | CUSTOM FABRICATION
752 | 1 | OPEN STORAGE CABINET | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION PART OF ITEM #751 WITH ADJUSTABLE SHELF
753 | 1 | RICE WARMER | 230 | 1 | 0.2
754 | 1 | RICE WARMER STAND | [16 empty] | CUSTOM FABRICATION MOBILE
755 | - | SPARE NUMBER
756 | 1 | NORI WARMER | 230 | 1 | 0.1
757 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION PART OF ITEM #751
758 | 1 | SUSHI CASE | 230 | 1 | 5 | [13 empty] | CUSTOM FABRICATION REMOTE REFRIGERATION
759 | - | SPARE NUMBER
760 | - | SPARE NUMBER
761 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #751
762 | 1 | PREPARATION SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #751
763 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION PART OF ITEM #751
764 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #751
765 | - | SPARE NUMBER
766 | 1 | OPEN STORAGE CABINET | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION PART OF ITEM #751 WITH ADJUSTABLE SHELF
767 | 1 | RICE WARMER | 230 | 1 | 0.2
768 | 1 | RICE WARMER STAND | [16 empty] | CUSTOM FABRICATION MOBILE
769 | - | SPARE NUMBER
770 | - | SPARE NUMBER
771 | 1 | NORI WARMER | 230 | 1 | 0.1
772 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION WATER COOLED PART OF ITEM #751
773 | 1 | PREPARATION SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #751
774 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION WATER COOLED PART OF ITEM #751
775 | - | SPARE NUMBER
776 | 1 | RECESSED CUTTING BOARD | [16 empty] | CUSTOM FABRICATION PART OF ITEM #751
777 | 1 | OPEN STORAGE CABINET | 230 | 1 | 10 | [13 empty] | CUSTOM FABRICATION PART OF ITEM #751 WITH ADJUSTABLE SHELF
778 | 1 | RICE WARMER | 230 | 1 | 0.2
779 | - | SPARE NUMBER
780 | - | SPARE NUMBER
781 | 1 | RICE WARMER STAND | [16 empty] | CUSTOM FABRICATION MOBILE
782 | 1 | NORI WARMER | 230 | 1 | 0.1
783 | 1 | UNDERCOUNTER REFRIGERATOR WITH SLIDING GLASS DOORS AND PAN SLIDES | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION REMOTE REFRIGERATION WATER COOLED PART OF ITEM #751
784 | 1 | PREPARATION SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #751
785 | - | SPARE NUMBER
786 | 1 | SUSHI BAR TOP AND DIE | [16 empty] | MILLWORK / BY INTERIOR DESIGNER
787 | - | SPARE NUMBER
788 | - | SPARE NUMBER
789 | - | SPARE NUMBER
790- 800 | - | SPARE NUMBERS
BAR AREA
801 | 1 | BAR TOP AND DIE | [16 empty] | MILLWORK / BY INTERIOR DESIGNER WITH DRINK RAIL
802 | 1 | BAR WORK COUNTER | [16 empty] | CUSTOM FABRICATION
803 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 | 40 | [9 empty] | CUSTOM FABRICATION WITH SOAP AND TOWEL DISPENSER PART OF ITEM #802
804 | 1 | UNDERCOUNTER FREEZER | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
805 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
806 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
807 | 1 | POS SYSTEM | 230 | 1 | 10 | [13 empty] | BY OS&E
808 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #802
809 | - | SPARE NUMBER
810 | - | SPARE NUMBER
811 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
812 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
813 | 1 | BLENDER STATION | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
814 | 1 | BAR BLENDER | 230 | 1 | 3.5 | [13 empty] | WITH DOME
815 | - | SPARE NUMBER
816 | 1 | CO2 GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #802
817 | 1 | CO2 TANK | [16 empty] | BY VENDOR
818 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERS WATER COOLED PART OF ITEM #802
819 | - | SPARE NUMBER
820 | - | SPARE NUMBER
821 | 1 | STAIR STEP REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #802
822 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
823 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
824 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #802
825 | - | SPARE NUMBER
826 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
827 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
828 | 1 | BLENDER STATION | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
829 | - | SPARE NUMBER
830 | - | SPARE NUMBER
831 | 1 | BAR BLENDER | 230 | 1 | 3.5 | [13 empty] | WITH DOME
832 | 1 | CO2 GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #802
833 | 1 | CO2 TANK | [16 empty] | BY VENDOR
834 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERSWATER COOLED PART OF ITEM #802
835 | - | SPARE NUMBER
836 | 1 | STAIR STEP REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #802
837 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
838 | 1 | UNDERCOUNTER FREEZER WITH CARVING BOARD TOP | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
839 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
840 | - | SPARE NUMBER
841 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
842 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERS PART OF ITEM #802
843 | 1 | STAIR STEP REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #802
844 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
845 | - | SPARE NUMBER
846 | 1 | CO2 GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #802
847 | 1 | CO2 TANK | [16 empty] | BY VENDOR
848 | 1 | BLENDER STATION | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
849 | - | SPARE NUMBER
850 | - | SPARE NUMBER
851 | 1 | BAR BLENDER | 230 | 1 | 3.5 | [13 empty] | WITH DOME
852 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #802
853 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
854 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
855 | - | SPARE NUMBER
856 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
857 | 1 | POS SYSTEM | 230 | 1 | 10 | [13 empty] | BY OS&E
858 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
859 | - | SPARE NUMBER
860 | - | SPARE NUMBER
861 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 | 40 | [9 empty] | CUSTOM FABRICATION WITH SOAP AND TOWEL DISPENSER PART OF ITEM #802
862 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #802
863 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
864 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
865 | - | SPARE NUMBER
866 | 1 | BLENDER STATION | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
867 | 1 | BAR BLENDER | 230 | 1 | 3.5 | [13 empty] | WITH DOME
868 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION PART OF ITEM #802
869 | - | SPARE NUMBER
870 | - | SPARE NUMBER
871 | 1 | CO2 GLASS FROSTER | [16 empty] | MOUNTED TO ITEM #802
872 | 1 | CO2 TANK | [16 empty] | BY VENDOR
873 | 1 | STAIR STEP REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #802
874 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #802
875 | - | SPARE NUMBER
876 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
877 | 1 | UNDERCOUNTER FREEZER WITH CARVING BOARD | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
878 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
879 | - | SPARE NUMBER
880 | - | SPARE NUMBER
881 | 1 | UNDERCOUNTER FREEZER | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOOR PART OF ITEM#802
882 | 1 | FLIP TOP WITH DOOR | [16 empty] | MILLWORK / BY INTERIOR DESIGNER PART OF ITEM#801
883 | - | SPARE NUMBER
884 | - | SPARE NUMBER
885 | - | SPARE NUMBER
886 | 1 | BACK BAR TOP WITH BOTTLE STEP | [16 empty] | MILLWORK / BY INTERIOR DESIGNER
887 | 1 | UNDERCOUNTER PASS-THRU REFRIGERATOR | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WATER COOLED WITH DOORS PART OF ITEM #886
888 | - | SPARE NUMBER
889 | - | SPARE NUMBER
890 | - | SPARE NUMBER
891 | - | SPARE NUMBER
892 | - | SPARE NUMBER
893 | - | SPARE NUMBER
894 | - | SPARE NUMBER
895- 900 | - | SPARE NUMBERS
PDR BAR AREA
901 | 1 | BAR TOP AND DIE WITH DRINK RAIL | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR WITH GLASS TROUGH
902 | 1 | BAR WORK COUNTER | [16 empty] | CUSTOM FABRICATION
903 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 | 40 | [9 empty] | CUSTOM FABRICATION WITH SOAP AND TOWEL DISPENSER PART OF ITEM #902
904 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 |  |  |  | 25 | [9 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
905 | - | SPARE NUMBER
906 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #902
907 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #902
908 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
909 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
910 | - | SPARE NUMBER
911 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERS WATER COOLED PART OF ITEM #902
912 | 1 | REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #902
913 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #902
914 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
915 | - | SPARE NUMBER
916 | 1 | POS SYSTEM | 230 | 1 | 10 | [13 empty] | BY OS&E
917 | - | SPARE NUMBER
918 | - | SPARE NUMBER
919 | - | SPARE NUMBER
920 | - | SPARE NUMBER
921 | 1 | BACK BAR WORK COUNTER | [16 empty] | CUSTOM FABRICATION
922 | 1 | BACK BAR TOP | [16 empty] | BY INTERIOR DESIGNER
923 | 1 | OPEN STORAGE CABINET | 230 | 1 | 10 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
924 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 |  |  |  | 25 | [9 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
925 | - | SPARE NUMBER
926 | 1 | STORAGE CABINET | 230 | 1 | 10 | [13 empty] | MILLWORK / BY GENERAL CONTRACTOR
927 | 1 | BOTTLE DISPLAY | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
928 | - | SPARE NUMBER
929 | - | SPARE NUMBER
930- 950 | - | SPARE NUMBER
CIGAR LOUNGE BAR AREA
951 | 1 | BAR TOP AND DIE WITH DRINK RAIL | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR WITH GLASS TROUGH
952 | 1 | BAR WORK COUNTER | [16 empty] | CUSTOM FABRICATION
953 | 1 | HAND SINK |  |  |  | 15 | 15 | 20 | 40 | [9 empty] | CUSTOM FABRICATION WITH SOAP AND TOWEL DISPENSER PART OF ITEM #952
954 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 |  |  |  | 25 | [9 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
955 | - | SPARE NUMBER
956 | 1 | UTILITY SINK |  |  |  | 15 | 15 | 55 | 40 | [9 empty] | CUSTOM FABRICATION PART OF ITEM #952
957 | 1 | TRASH CHUTE | [16 empty] | CUSTOM FABRICATION PART OF ITEM #952
958 | 1 | TRASH RECEPTACLE | [16 empty] | SLIM JIM
959 | 1 | FLOOR GULLY & GRATE | [7 empty] | 50 | [8 empty] | BY MEP
960 | - | SPARE NUMBER
961 | 1 | REFRIGERATED COCKTAIL STATION | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION WITH ICE DIVIDERS WATER COOLED PART OF ITEM #952
962 | 1 | REFRIGERATED CONDIMENT RAIL | 230 | 1 | 5 |  |  |  | 25 | [7 empty] | 15 | 15 | CUSTOM FABRICATION DOUBLE HEIGHT WATER COOLED PART OF ITEM #952
963 | 1 | DOUBLE BOTTLE RAIL | [16 empty] | CUSTOM FABRICATION PART OF ITEM #952
964 | 1 | P.O.S. PRINTER | 230 | 1 | 5 | [13 empty] | BY OS&E
965 | - | SPARE NUMBER
966 | 1 | POS SYSTEM | 230 | 1 | 10 | [13 empty] | BY OS&E
967 | - | SPARE NUMBER
968 | - | SPARE NUMBER
969 | - | SPARE NUMBER
970 | - | SPARE NUMBER
971 | - | SPARE NUMBER
972 | - | SPARE NUMBER
973 | 1 | BACK BAR TOP | [16 empty] | BY INTERIOR DESIGNER
974 | 1 | UNDERCOUNTER REFRIGERATOR | 230 | 1 | 1.64 |  |  |  | 25 | [9 empty] | CUSTOM FABRICATION WITH DOORS WATER COOLED
975 | - | SPARE NUMBER
976 | 1 | BACK BAR WORK COUNTER | [16 empty] | CUSTOM FABRICATION
977 | 1 | BOTTLE DISPLAY | [16 empty] | MILLWORK / BY GENERAL CONTRACTOR
978 | - | SPARE NUMBER
979 | - | SPARE NUMBER
980- 1000 | - | SPARE NUMBER
Total