## Sheet
________ Preliminary Utility Schedule
August 05, 2024
NO | QTY | DESCRIPTION | VOLTS | PH | AMPS | KW | CW | HW | GPH | IW | DW | BTUS | EXH CFM | SUPPLY CFM | HEAT REJECTION | CHILLED WATER IN | CHILLED WATER OUT | REMARKS
PREPARATION AREA
1 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
2 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
3 | 1 | SUSHI PREPARATION TABLE WITH SINK | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
4 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
5 | - | SPARE NUMBER
6 | 2 | RICE WARMER STAND | [15 empty] | CUSTOM FABRICATION MOBILE
7 | 2 | RICE COOKER WITH WARMER | 120 | 1 | 18
8 | 1 | INGREDIENT BIN | [15 empty] | MOBILE
9 | - | SPARE NUMBER
10 | - | SPARE NUMBER
11 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
12 | 1 | VEGETABLE PREPARATION TABLE WITH SINKS | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
13 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
14 | 1 | CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #12
15 | - | SPARE NUMBER
16 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
17 | 1 | CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #12
18 | 1 | MEAT PREPARATION TABLE WITH SINK | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
19 | - | SPARE NUMBER
20 | - | SPARE NUMBER
21 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
22 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
23 | 1 | CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #18
24 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
25 | - | SPARE NUMBER
26 | 1 | FISH PREPARATION TABLE WITH SINKS | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
27 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
28 | 1 | KNIFE SANITIZER | 120 | 1 | 10 | [12 empty] | WALL MOUNTED
29 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
30 | - | SPARE NUMBER
31 | 1 | FISH SINK | [7 empty] | 1-1/2" | [7 empty] | CUSTOM FABRICATION PART OF ITEM #26
32 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
33 | 1 | FISH SINK | [7 empty] | 1-1/2" | [7 empty] | CUSTOM FABRICATION PART OF ITEM #26
34 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
35-40 | - | SPARE NUMBER
WAREWASH AREA
41 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
42 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
43 | 1 | POT SINK |  |  |  |  | (2)3/4" | 3/4" | 90 | (3)2" | [7 empty] | CUSTOM FABRICATION
44 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
45 | - | SPARE NUMBER
46 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
47 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
48 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
49 | - | SPARE NUMBER
50 | - | SPARE NUMBER
51 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
52 | 1 | HOSE REEL | [15 empty] | CEILING MOUNT
53 | 1 | HOSE REEL CONTROL CABINET |  |  |  |  | 1/2" | 1/2" | 25 | [8 empty] | FOR ITEM #52
54 | 1 | MOP SINK CABINET |  |  |  |  | 1/2" | 1/2" | 30 |  | 2"
55 | - | SPARE NUMBER
56 | 1 | DISH DROP WINDOW WITH SHELF | [15 empty] | CUSTOM FABRICATION
57 | 1 | SOILED DISH TABLE | [15 empty] | CUSTOM FABRICATION
58 | 3 | SILVERWARE CHUTE | [15 empty] | CUSTOM FABRICATION
59 | - | SPARE NUMBER
60 | - | SPARE NUMBER
61 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #341
62 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
63 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
64 | 1 | DISH MACHINE | 208 | 3 | 51 |  | (2)1/2" |  |  | 2" |  |  |  |  | 6100 |  |  | 180°F RINSE VENTLESS
65 | - | SPARE NUMBER
66 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
67 | 1 | HOSE REEL | [15 empty] | CEILING MOUNT
68 | 1 | HOSE REEL CONTROL CABINET |  |  |  |  | 1/2" | 1/2" | 25 | [8 empty] | FOR ITEM #67
69 | - | SPARE NUMBER
70 | - | SPARE NUMBER
71 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
72 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
73 | 1 | UNDERCOUNTER DISH MACHINE | 120 | 1 | 30.5 |  | 1/2" |  |  | 1-1/2" | [7 empty] | 180°F RINSE VENTLESS
74 | 2 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
75-80 | - | SPARE NUMBER
PASTRY PREPARATION AREA
81 | 1 | PASS THRU SHELF | [15 empty] | CUSTOM FABRICATION
82 | 1 | PASTRY PREPARATION COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
83 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #82
84 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
85 | - | SPARE NUMBER
86 | 1 | DIPPERWELL | [5 empty] | 1/2" | 5 | 1-1/2"
87 | 1 | MARBLE TOP | [15 empty] | CUSTOM FABRICATION PART OF ITEM #82
88 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #82
89 | - | SPARE NUMBER
90 | - | SPARE NUMBER
91 | 1 | PASTRY PREPARATION TABLE | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
92 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
93 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | CUSTOM FABRICATION PART OF ITEM #91
94 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #91
95 | - | SPARE NUMBER
96 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
97 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #91
98 | 1 | BLENDER | 120 | 1 | 13
99 | - | SPARE NUMBER
100 | - | SPARE NUMBER
101 | 1 | 5 QT. MIXER | 120 | 1 | 2.9
102 | 1 | INDUCTION WARMER | 208 | 1 | 22 | [12 empty] | 2 RING
103 | 1 | COUNTERTOP FRYER | 208 | 3 | 20.8
104 | 1 | COUNTERTOP COMBI OVEN | 208 | 3 | 16.5 |  |  |  | 1 | 1 1/2"
105-110 | - | SPARE NUMBER
SERVICE BAR AREA
111 | 1 | BEVERAGE TABLE WITH SINK | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
112 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
113 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #111
114 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
115 | - | SPARE NUMBER
116 | 1 | REFRIGERATED CONDIMENT RAIL | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION PART OF #111
117 | 1 | COCKTAIL STATION | [7 empty] | 1" | [7 empty] | CUSTOM FABRICATION PART OF #111
118 | 1 | DOUBLE BOTTLE RAIL | [15 empty] | CUSTOM FABRICATION PART OF ITEM #111
119 | - | SPARE NUMBER
120 | - | SPARE NUMBER
121 | 1 | PASS THRU SHELF | [15 empty] | CUSTOM FABRICATION
122 | 1 | SINK |  |  |  |  | 1/2" | 1/2" | 30 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
123 | 1 | GLASS RINSER | [7 empty] | 1/2"
124 | 1 | ESPRESSO MACHINE | 120 | 1 | 13 |  | 3/8" |  |  | 1-1/4"
125 | - | SPARE NUMBER
126 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2.7 | [12 empty] | MOBILE
127 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
128 | 2 | ESPRESSO GRINDER | 120 | 1 | 5.4
129 | - | SPARE NUMBER
130 | - | SPARE NUMBER
131 | 1 | KNOCK BOX | [15 empty] | CUSTOM FABRICATION PART OF ITEM #111
132 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
133 | 1 | COFFEE GRINDER | 120 | 1 | 3.5
134 | 1 | COFFEE BREWER | 120 | 1 | 28.3 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
135 | - | SPARE NUMBER
136 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2.7 | [12 empty] | MOBILE
137 | 1 | HOT WATER DISPENSER | 120 | 1 | 15 |  | 1/4"
138 | 1 | SAKE WARMER | 120 | 1 | 15
139 | - | SPARE NUMBER
140 | - | SPARE NUMBER
141 | 1 | GLASS FILLER SINK |  |  |  |  | 3/8" |  |  | 3/4"
142 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
143 | 1 | SINK |  |  |  |  | 1/2" | 1/2" | 30 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
144 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #111
145 | - | SPARE NUMBER
146 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
147 | 2 | WINE REFRIGERATOR | 120 | 1 | 3
148 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 5.9 | [12 empty] | MOBILE
149 | - | SPARE NUMBER
150-160 | - | SPARE NUMBER
ICE AND STORAGE AREA
161 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #173
162 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #168
163 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #164
164 | 1 | ICE MACHINE | 120 | 1 | 11.5 |  | 3/8" |  |  | 3/4" |  |  |  |  | 4500 |  |  | 500LBS AIR COOLED LARGE CUBE STYLE
165 | - | SPARE NUMBER
166 | 1 | ICE BIN | [7 empty] | 3/4" | [7 empty] | 700LBS.
167 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
168 | 1 | ICE MACHINE | 208 | 1 | 14.5 |  | 1/2" |  |  | 3/4" |  |  |  |  | 21200 |  |  | 1875LBS. AIR-COOLED CUBE STYLE
169 | - | SPARE NUMBER
170 | - | SPARE NUMBER
171 | 1 | ICE BIN | [7 empty] | 3/4" | [7 empty] | 900LBS.
172 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
173 | 1 | ICE MACHINE | 120 | 1 | 15.2 |  | 1/2" |  |  | 3/4" |  |  |  |  | 8500 |  |  | 980LBS AIR-COOLED FLAKE STYLE
174 | 1 | ICE BIN | [7 empty] | 3/4" | [7 empty] | 500LBS.
175 | - | SPARE NUMBER
176 | 6 | DRY STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
177 | 1 | WALK-IN COOLER | 120 | 1 | 20
178 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
179 | - | SPARE NUMBER
180 | - | SPARE NUMBER
181 | 2 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
182 | 1 | COOLER CONDENSING UNIT | 208 | 3 | 4.7 | [10 empty] | 1/2" | 1/2" | ON EMERGENCY POWER FOR ITEM #177
183 | 10 | COOLER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
184 | 1 | WALK-IN FREEZER | 120 | 1 | 20
185 | - | SPARE NUMBER
186 | 1 | EVAPORATOR COIL | 208 | 1 | 9.1 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
187 | 1 | FREEZER CONDENSING UNIT | 208 | 3 | 11.4 | [10 empty] | 1/2" | 1/2" | ON EMERGENCY POWER FOR ITEM #184
188 | 4 | FREEZER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
189 | - | SPARE NUMBER
190-200 | - | SPARE NUMBER
COOKING AREA
201 | 1 | PASS THRU SHELF | [15 empty] | CUSTOM FABRICATION
202 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #251
203 | 1 | HOOD CONTROL CABINET | 120 | 1 | 4 | [12 empty] | FOR ITEM #251
204 | 1 | CHEF'S COUNTER WITH SINKS | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
205 | - | SPARE NUMBER
206 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
207 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #204
208 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #204
209 | - | SPARE NUMBER
210 | - | SPARE NUMBER
211 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
212 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #204
213 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | CUSTOM FABRICATION PART OF ITEM #204
214 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #204
215 | - | SPARE NUMBER
216 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
217 | 1 | INDUCTION WARMER | 208 | 1 | 22 | [12 empty] | 2 RING
218 | 1 | INDUCTION WARMER | 120 | 1 | 14 | [12 empty] | 1 RING
219 | - | SPARE NUMBER
220 | - | SPARE NUMBER
221 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DOORS PART OF ITEM #204
222 | 1 | COUNTERTOP COMBI OVEN | 208 | 1 | 30 |  | 3/4" |  |  | 1 1/2"
223 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
224 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #204
225 | - | SPARE NUMBER
226 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #204
227 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
228 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | CUSTOM FABRICATION PART OF ITEM #204
229 | - | SPARE NUMBER
230 | - | SPARE NUMBER
231 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #204
232 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
233 | 1 | RICE COOKER WITH WARMER | 120 | 1 | 18
234 | 1 | UNDERCOUNTER PLATE WARMER | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION PART OF ITEM #204
235 | - | SPARE NUMBER
236 | 1 | DROP-IN HEATED SHELF | 120 | 1 | 7.4
237 | 1 | DROP-IN HEATED SHELF | 120 | 1 | 7.4
238 | - | SPARE NUMBER
239 | - | SPARE NUMBER
240-250 | - | SPARE NUMBER
251 | 1 | EXHAUST HOOD | 120 | 1 | 40 | [7 empty] | 5286 | 1586 |  |  |  | WITH MAKE-UP AIR
252 | 1 | COOKING SUITE
252A | 1 | MODULAR 6 BURNER RANGE | [9 empty] | 210000 | [5 empty] | PART OF ITEM #252
252B | 1 | OVEN BASE | 120 | 1 | 15 | [6 empty] | 40000 | [5 empty] | PART OF ITEM #252
252C | 1 | MODULAR CHARBROILER | [9 empty] | 120000 | [5 empty] | PART OF ITEM #252
252D | 1 | REFRIGERATED BASE | 120 | 1 | 11 | [12 empty] | PART OF ITEM #252
252E | 1 | LOAD CENTER | 120 | 1 | 60 | [12 empty] | PART OF ITEM #252
252F | 2 | FRYER | [9 empty] | 114000 | [5 empty] | PART OF ITEM #252
252G | 1 | 4 BURNER RANGE | [9 empty] | 140000 | [5 empty] | PART OF ITEM #252
252H | 1 | OVEN BASE | 120 | 1 | 15 | [6 empty] | 40000 | [5 empty] | PART OF ITEM #252
252J | 1 | SALAMANDER | [9 empty] | 20000 | [5 empty] | PART OF ITEM #252
253 | 1 | ROBATA GRILL | [15 empty] | ELECTRIC
254 | 1 | COMBI OVEN | 208 | 1 | 2.4 |  | 1/2" |  |  | 2" |  | 83500
255-300 | - | SPARE NUMBER
SUSHI AREA
301-400 | - | SPARE NUMBER
BAR AREA
401 | 1 | BAR TOP AND DIE | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR WITH DRINK RAIL
402 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
403 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | 1" | [6 empty] | 180°
404 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
405 | - | SPARE NUMBER
406 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
407 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
408 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
409 | - | SPARE NUMBER
410 | - | SPARE NUMBER
411 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
412 | 1 | BOTTLE STORAGE BIN | [7 empty] | 1/2"
413 | 1 | SPEED RAIL
414 | 1 | COCKTAIL STATION | [7 empty] | 1/2"
415 | - | SPARE NUMBER
416 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
417 | 2 | GLASS RINSER | [7 empty] | 1/2"
418 | 1 | REFRIGERATED CABINET | 120 | 1 | 1.9
419 | - | SPARE NUMBER
420 | - | SPARE NUMBER
421 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
422 | 1 | BOTTLE STORAGE BIN | [7 empty] | 1/2"
423 | 1 | SPEED RAIL
424 | 1 | COCKTAIL STATION | [7 empty] | 1/2"
425 | - | SPARE NUMBER
426 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
427 | 2 | GLASS RINSER | [7 empty] | 1/2"
428 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2"
429 | - | SPARE NUMBER
430 | - | SPARE NUMBER
431 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
432 | 1 | REFRIGERATED CABINET | 120 | 1 | 1.9
433 | - | SPARE NUMBER
434 | - | SPARE NUMBER
435-440 | - | SPARE NUMBER
441 | 1 | BACK BAR TOP | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
442 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 6.3 | [12 empty] | MOBILE
443 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
444 | 1 | POS SYSTEM | 120 | 1 | 20 | [12 empty] | BY OS&E
445 | - | SPARE NUMBER
446 | 1 | DRAFT BEER REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
447 | 1 | DRIP TRAY | [7 empty] | 1/2"
448 | 1 | BEER DISPENSING TOWER | [15 empty] | 2 TAP
449 | - | SPARE NUMBER
450 | - | SPARE NUMBER
451 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 6.3 | [12 empty] | MOBILE
452 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
453 | 1 | POS SYSTEM | 120 | 1 | 20 | [12 empty] | BY OS&E
454 | 1 | BOTTLE DISPLAY | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
455-500 | - | SPARE NUMBER
ROOM SERVICE AREA
501 | 1 | ORDER TAKER WORK SURFACE | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
502 | 1 | WALL CABINET | [15 empty] | CUSTOM FABRICATION
503 | 2 | CHAIR | [15 empty] | BY OS&E
504 | 2 | COMPUTER | 120 | 1 | 20 | [12 empty] | BY OWNER
505 | - | SPARE NUMBER
506 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
507 | 10 | ROOM SERVICE HOT BOXES | 120 | 1 | 1.3
508 | 8 | ROOM SERVICE TABLES | [15 empty] | MOBILE
509 | - | SPARE NUMBER
510 | - | SPARE NUMBER
511 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
512 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
513 | 1 | WORK TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
514 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
515 | - | SPARE NUMBER
516 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
517 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE
518 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.3 | [12 empty] | MOBILE
519 | - | SPARE NUMBER
520 | - | SPARE NUMBER
521 | 1 | POP-UP TOASTER | 120 | 1 | 15
522 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 3.8 | [12 empty] | MOBILE
523 | 1 | BEVERAGE COUNTER WITH SINK | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
524 | 1 | GLASS FILLER SINK |  |  |  |  | 3/8" |  |  | 3/4"
525 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  | 10 | [8 empty] | UNDER COUNTER FOR ITEM #526
526 | 1 | HOT WATER DISPENSER | 120 | 1 | 15 |  | 1/4"
527 | 1 | COFFEE AND TEA BREWER | 120 | 1 | 13 |  | 3/8" |  | 10
528 | 1 | KNOCK BOX | [15 empty] | CUSTOM FABRICATION PART OF ITEM #523 #527 #534
529 | - | SPARE NUMBER
530 | - | SPARE NUMBER
531 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
532 | 1 | COFFEE GRINDER | 120 | 1 | 3.5
533 | 1 | ESPRESSO GRINDER | 120 | 1 | 7.5
534 | 1 | ESPRESSO MACHINE | 120 | 1 | 13 |  | 3/8" |  |  | 1-1/4"
535 | - | SPARE NUMBER
536 | 2 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
537 | - | SPARE NUMBER
538 | - | SPARE NUMBER
539 | - | SPARE NUMBER
540 | - | SPARE NUMBER
PASTRY PREPARATION AND OFFICE AREA
541 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
542 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
543 | 1 | BATCH ICE CREAM FREEZER | 208 | 3 | 28 |  | 1/2" |  |  | 1/2" | [7 empty] | MOBILE
544 | 1 | PASTRY COUNTER WITH SINK | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
545 | - | SPARE NUMBER
546 | 1 | WALL CABINET | [15 empty] | CUSTOM FABRICATION
547 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #544
548 | 1 | INDUCTION WARMER | 208 | 1 | 22 | [12 empty] | 2 RING
549 | - | SPARE NUMBER
550 | - | SPARE NUMBER
551 | 1 | COUNTERTOP FRYER | 208 | 3 | 20.8
552 | 1 | COUNTERTOP COMBI OVEN | 208 | 3 | 16.5 |  |  |  | 1 | 1 1/2"
553 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
554 | 2 | INGREDIENT BIN | [15 empty] | MOBILE
555 | - | SPARE NUMBER
556 | 2 | PORTION SCALE | 120 | 1 | 5
557 | 1 | 5 QT. MIXER | 120 | 1 | 2.9
558 | 1 | CHOCOLATE MELTING MACHINE | 120 | 1 | 3.3
559 | - | SPARE NUMBER
560 | - | SPARE NUMBER
561 | 1 | DIPPERWELL | [5 empty] | 1/2" | 5 | 1-1/2"
562 | 1 | ICE CREAM FREEZER | 120 | 1 | 3.5 | [6 empty] | 1433
563 | 1 | MARBLE TOP | [15 empty] | CUSTOM FABRICATION PART OF ITEM #544
564 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #544
565 | - | SPARE NUMBER
566 | 1 | PASS THRU SHELF | [15 empty] | CUSTOM FABRICATION
567 | - | SPARE NUMBER
568 | - | SPARE NUMBER
569 | - | SPARE NUMBER
570-580 | - | SPARE NUMBER
581 | 1 | WORK SURFACE | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
582 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
583 | 2 | CHAIR | [15 empty] | BY OS&E
584 | 2 | COMPUTER | 120 | 1 | 20 | [12 empty] | BY OWNER
585 | - | SPARE NUMBER
586 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
587 | - | SPARE NUMBER
588 | - | SPARE NUMBER
589 | - | SPARE NUMBER
590-600 | - | SPARE NUMBER
COOKING AREA
601 | 1 | PASTRY COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
602 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
603 | 1 | MARBLE TOP | [15 empty] | CUSTOM FABRICATION
604 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #601
605 | 1 | INDUCTION WARMER | 208 | 1 | 22 | [12 empty] | 2 RING
606 | 1 | COUNTERTOP COMBI OVEN | 208 | 3 | 16.5 |  |  |  | 1 | 1 1/2"
607 | 2 | INGREDIENT BIN | [15 empty] | MOBILE
608 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
609 | - | SPARE NUMBER
610 | - | SPARE NUMBER
611 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
612 | 1 | EXHAUST HOOD | 120 | 1 | 40 | [7 empty] | 5286 | 1586 |  |  |  | WITH MAKE-UP AIR
613 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #612
614 | 1 | HOOD CONTROL CABINET | 120 | 1 | 4 | [12 empty] | FOR ITEM #612
615 | - | SPARE NUMBER
616 | 1 | DOUBLE COMBI OVEN | [15 empty] | MOBILE
617 | 2 | FRYER | [9 empty] | 100000 | [5 empty] | MOBILE
618 | 1 | PASTA COOKER |  |  |  |  | 1/2" |  |  | 1" |  | 80000 | [5 empty] | MOBILE
619 | - | SPARE NUMBER
620 | - | SPARE NUMBER
621 | 2 | MODULAR 6 BURNER RANGE | [9 empty] | 210000
622 | 1 | FILL FAUCET |  |  |  |  | 3/4" | 3/4" | 30
623 | 1 | FREEZER BASE | 120 | 1 | 11 | [12 empty] | MOBILE
624 | 1 | SALAMANDER | [9 empty] | 20000 | [5 empty] | WALL MOUNTED
625 | - | SPARE NUMBER
626 | 1 | MODULAR CHARBROILER | [9 empty] | 120000
627 | 1 | MODULAR PLANCHA
628 | 1 | REFRIGERATED BASE | 120 | 1 | 1.8 |  |  |  |  | 1" |  | 2800 | [5 empty] | MOBILE
629 | - | SPARE NUMBER
630 | - | SPARE NUMBER
631 | 1 | STONE HEARTH OVEN | 120 | 1 | 2 | [6 empty] | 55000 | [5 empty] | WITH HOOD
632 | 1 | CHEFS COUNTER WITH SINK | 120 | 1 | 80 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
633 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #632
634 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | CUSTOM FABRICATION PART OF ITEM #632
635 | - | SPARE NUMBER
636 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #632
637 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
638 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
639 | - | SPARE NUMBER
640 | - | SPARE NUMBER
641 | 1 | CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #632
642 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #632
643 | 1 | CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #632
644 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #632
645 | - | SPARE NUMBER
646 | 1 | DROP-IN HOT FOOD WELL | 208 | 1 | 6 |  |  | 1/2" | 5 | 1/2" | [7 empty] | 2 WELLS AUTOFILL
647 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
648 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #632
649 | - | SPARE NUMBER
650-660 | - | SPARE NUMBER
WAREWASH AREA
661 | 1 | DISH DROP WINDOW WITH SHELF | [15 empty] | CUSTOM FABRICATION
662 | 3 | SILVERWARE CHUTE | [15 empty] | CUSTOM FABRICATION
663 | 1 | CLEAN DISH TABLE WITH SINK | [15 empty] | CUSTOM FABRICATION
664 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #663
665 | - | SPARE NUMBER
666 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
667 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
668 | 1 | DISH MACHINE | 208 | 3 | 51 |  | (2)1/2" |  |  | 2" |  |  |  |  | 6100 |  |  | 180°F RINSE VENTLESS
669 | - | SPARE NUMBER
670 | - | SPARE NUMBER
671 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
672 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
673 | 1 | UNDERCOUNTER DISH MACHINE | 120 | 1 | 30.5 |  | 1/2" |  |  | 1-1/2" | [7 empty] | 180°F RINSE VENTLESS
674 | 1 | MOP SINK CABINET |  |  |  |  | 1/2" | 1/2" | 30 |  | 2"
675 | - | SPARE NUMBER
676 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
677 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
678 | 1 | POT SINK |  |  |  |  | (2)3/4" | 3/4" | 90 | (3)2" | [7 empty] | CUSTOM FABRICATION
679 | - | SPARE NUMBER
680 | - | SPARE NUMBER
681 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
682 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
683 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
684 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
685 | - | SPARE NUMBER
686 | - | SPARE NUMBER
687 | 2 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
688 | - | SPARE NUMBER
689 | - | SPARE NUMBER
690 | - | SPARE NUMBER
691 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
692 | 1 | WALK-IN COOLER | 120 | 1 | 20
693 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
694 | 1 | COOLER CONDENSING UNIT | 208 | 3 | 4.7 | [10 empty] | 1/2" | 1/2" | ON EMERGENCY POWER FOR ITEM #693
695 | - | SPARE NUMBER
696 | 5 | COOLER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
697 | - | SPARE NUMBER
698 | - | SPARE NUMBER
699 | - | SPARE NUMBER
700 | - | SPARE NUMBER
BEVERAGE AREA
701 | 1 | BEVERAGE COUNTER WITH SINK | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
702 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
703 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
704 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | CUSTOM FABRICATION
705 | - | SPARE NUMBER
706 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
707 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
708 | 1 | KNOCK BOX | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
709 | - | SPARE NUMBER
710 | - | SPARE NUMBER
711 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
712 | 1 | COFFEE GRINDER | 120 | 1 | 3.5
713 | 2 | ESPRESSO GRINDER | 120 | 1 | 7.5
714 | 1 | ESPRESSO MACHINE | 120 | 1 | 13 |  | 3/8" |  |  | 1-1/4"
715 | - | SPARE NUMBER
716 | 1 | COFFEE AND TEA BREWER | 120 | 1 | 13 |  | 3/8" |  | 10
717 | 1 | HOT WATER DISPENSER | 120 | 1 | 15 |  | 1/4"
718 | 1 | SAKE WARMER | 120 | 1 | 15
719 | - | SPARE NUMBER
720 | - | SPARE NUMBER
721 | 2 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE
722 | 2 | UNDERCOUNTER FREEZER | 120 | 1 | 2.3 | [12 empty] | MOBILE
723 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  | 10 | [8 empty] | UNDER COUNTER FOR ITEM #714 #716. #717
724 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE
725 | - | SPARE NUMBER
726 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
727 | - | SPARE NUMBER
728 | - | SPARE NUMBER
729 | - | SPARE NUMBER
730 | - | SPARE NUMBER
BAR AREA
731 | 1 | BAR TOP AND DIE
732 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2"
733 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
734 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
735 | - | SPARE NUMBER
736 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
737 | 1 | BOTTLE STORAGE BIN | [7 empty] | 1/2"
738 | 1 | SPEED RAIL
739 | - | SPARE NUMBER
740 | - | SPARE NUMBER
741 | 1 | COCKTAIL STATION | [7 empty] | 1/2"
742 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
743 | 2 | GLASS RINSER | [7 empty] | 1/2"
744 | 1 | REFRIGERATED CABINET | 120 | 1 | 1.9
745 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
746 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2"
747 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | 1" | [6 empty] | 180°
748 | 1 | BACK BAR
749 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
750 | - | SPARE NUMBER
751 | 2 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
752 | 2 | POS SYSTEM | 120 | 1 | 20 | [12 empty] | BY OS&E
753 | 1 | DRAFT BEER REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
754 | 1 | DRIP TRAY | [7 empty] | 1/2"
755 | - | SPARE NUMBER
756 | 1 | BEER DISPENSING TOWER | [15 empty] | 2 TAP
757 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
758 | 1 | BOTTLE DISPLAY | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
759 | - | SPARE NUMBER
760-770 | - | SPARE NUMBER
BAR SUPPORT PANTRY
771 | 3 | WINE REFRIGERATOR | 120 | 1 | 3
772 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #776
773 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #781
774 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
775 | - | SPARE NUMBER
776 | 1 | ICE MACHINE | 120 | 1 | 11.5 |  | 3/8" |  |  | 3/4" |  |  |  |  | 4500 |  |  | 500LBS AIR COOLED LARGE CUBE STYLE
777 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 2100 LBS.
778 | 2 | ICE CART | [15 empty] | MOBILE 250LBS
779 | - | SPARE NUMBER
780 | - | SPARE NUMBER
781 | 1 | ICE MACHINE | 120 | 1 | 15.2 |  | 1/2" |  |  | 3/4" |  |  |  |  | 8500 |  |  | 980LBS AIR-COOLED FLAKE STYLE
782 | - | SPARE NUMBER
783 | - | SPARE NUMBER
784 | - | SPARE NUMBER
785-800 | - | SPARE NUMBER
Total