## Sheet
________ Preliminary Utility Schedule
August 05, 2024
NO | QTY | DESCRIPTION | VOLTS | PH | AMPS | KW | CW | HW | GPH | IW | DW | BTUS | EXH CFM | SUPPLY CFM | HEAT REJECTION | CHILLED WATER IN | CHILLED WATER OUT | REMARKS
DOCK AREA
1-100 | - | SPARE NUMBERS
BULK STORAGE AREA
101 | 2 | SODA SYSTEM AND RACK | 120 | 1 | 20 |  | 1/2" | [10 empty] | BY VENDOR
102 | 3 | CO2 TANK | [15 empty] | BY VENDOR
103 | 1 | BULK FREEZER | 120 | 1 | 20
104 | 1 | EVAPORATOR COIL | 208 | 1 | 9.1 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
105 | - | SPARE NUMBER
106 | 4 | FREEZER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
107 | 1 | BULK COOLER | 120 | 1 | 20
108 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
109 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
110 | 1 | BLAST CHILLER | 120 | 1 | 20
111 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
112 | 5 | COOLER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
113 | 2 | DUNNAGE RACK
114 | 11 | DRY STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
115 | 1 | BLAST CHILLER EVAPORATOR COIL | 208 | 1 | 20.2
116 | 1 | ORDER TAKER WORK SURFACE | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
117 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
118 | 1 | CHAIR | [15 empty] | BY OS&E
119 | - | SPARE NUMBER
120 | - | SPARE NUMBER
121 | 1 | COMPUTER | 120 | 1 | 10 | [12 empty] | BY OS&E
122 | 1 | STORAGE CABINET - LOCKABLE | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
123 | - | SPARE NUMBER
124 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #128
125 | - | SPARE NUMBER
126 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 2000LBS.
127 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
128 | 1 | ICE MACHINE | 208 | 3 | 11.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 4000 | 3/8" | 1/2" | 1444LBS. WATER-COOLED CUBE ICE
129 | - | SPARE NUMBER
130 | - | SPARE NUMBER
131 | 1 | ICE MACHINE | 120 | 1 | 14.4 |  | 3/8" |  |  | 3/4" |  |  |  |  | 1000 | 3/8" | 1/2" | 500LBS. WATER-COOLED FLAKE ICE
132 | 3 | ICE CART | [15 empty] | MOBILE 250LBS.
133 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #131
134 | - | SPARE NUMBER
135 | - | SPARE NUMBER
136 | 2 | BEVERAGE STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
137 | 1 | BEER SYSTEM SHELF
138 | 1 | BEER SYSTEM | 120 | 1 | 3.5 | [10 empty] | 3/8" | 3/8" | WATER-COOLED
139 | - | SPARE NUMBER
140 | - | SPARE NUMBER
141 | 1 | WINE STORAGE SHELVING | [15 empty] | FIXED FOURTEEN TIER
142 | 1 | BEVERAGE COOLER | 120 | 1 | 20
143 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
144 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
145 | - | SPARE NUMBER
146 | 2 | KEG RACK | [15 empty] | 2 TIER 6 KEGS
147 | 4 | BEVERAGE STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
148 | 1 | WINE STORAGE SHELVING | [15 empty] | FIXED FOURTEEN TIER
149 | - | SPARE NUMBER
150 | - | SPARE NUMBER
151 | 4 | BANQUET HEATED CABINET | 120 | 1 | 10.8 | [12 empty] | MOBILE
152 | 6 | UTILITY RACK | [15 empty] | MOBILE
153 | 6 | PLATE RACK DOLLY | [15 empty] | MOBILE
154 | - | SPARE NUMBER
155-160 | - | SPARE NUMBERS
JANITOR/TRASH HOLD AREA
161 | 2 | TRASH TRUCK | [15 empty] | MOBILE
162 | 3 | RECYCLING CONTAINER | [15 empty] | MOBILE BLUE
163 | 1 | INSECT CONTROL | 120 | 1 | 1.4 | [12 empty] | WALL MOUNTED BY VENDOR
164 | - | SPARE NUMBER
165 | - | SPARE NUMBER
166 | 1 | MOP RACK | [15 empty] | BY GENERAL CONTRACTOR
167 | 1 | MOP SINK | [8 empty] | 2" | [6 empty] | BY GENERAL CONTRACTOR
168 | 1 | WALL SHELF | [15 empty] | CUSTOM FABRICATION
169 | - | SPARE NUMBER
170 | - | SPARE NUMBER
171 | 1 | HOSE BIBB |  |  |  |  | 1/2" | 1/2" | [9 empty] | BY GENERAL CONTRACTOR
172 | 1 | REVERSE OSMOSIS SYSTEM |  |  |  |  | 3/8" |  | 10.3 | 1/4" | [7 empty] | 250 GPD WITH STORAGE TANK FOR ITEM #263
173 | 1 | REVERSE OSMOSIS STORAGE TANK |  |  |  |  | 1/2" | [10 empty] | 40 GALLON FOR ITEM #172
174 | 3 | DETERGENT STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
175-190 | - | SPARE NUMBERS
REMOTE EQUIPMENT AREA
191 | 1 | REFRIGERATION RACK | 208 | 3 | 33.2 | [12 empty] | OUTDOOR AIR-COOLED ON EMERGENCY POWER
192-200 | - | SPARE NUMBER
ROOMSERVICE AREA
201 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 5.9 | [12 empty] | MOBILE
202 | 1 | ROOM SERVICE COUNTER WITH SINK | 120 | 1 | 40 |  |  |  | 15 | [8 empty] | CUSTOM FABRICATION
203 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
204 | 1 | GLASS FILLER STATION |  |  |  |  | 1/2" |  |  | 3/4"
205 | - | SPARE NUMBER
206 | 3 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
207 | 1 | COFFEE BREWER | 208 | 1 | 19.7 |  | 3/8"
208 | 1 | COFFEE GRINDER | 120 | 1 | 9.4
209 | - | SPARE NUMBER
210 | - | SPARE NUMBER
211 | 1 | ICED TEA BREWER | 120 | 1 | 18 |  | 3/8"
212 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
213 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
214 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
215 | - | SPARE NUMBER
216 | 8 | HOT BOX | 120 | 1 | 2.5
217 | 1 | ROOM SERVICE HOT BOX STORAGE RACK
218 | 4 | ROOM SERVICE TABLES
219 | - | SPARE NUMBER
220 | - | SPARE NUMBER
221 | 1 | WORK SURFACE | 120 | 1 | 20 | [12 empty] | MILLWORK / BY GENERAL CONTRACTOR
222 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
223 | 1 | CHAIR | [15 empty] | BY OS&E
224 | 1 | COMPUTER | 120 | 1 | 10 | [12 empty] | BY OS&E
225 | - | SPARE NUMBER
226 | 1 | CHAIR | [15 empty] | BY OS&E
227 | 1 | COMPUTER | 120 | 1 | 10 | [12 empty] | BY OS&E
228 | 1 | STORAGE CABINET - LOCKABLE | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
229 | - | SPARE NUMBER
230 | - | SPARE NUMBER
BULK PREPARATION/COOKING AREA
231 | 1 | BULK PREPARATION COUNTER WITH SINK AND MIXER RECESS | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
232 | 1 | 20QT. MIXER | 120 | 1 | 8
233 | 1 | MIXER ATTACHMENT SHELF | [15 empty] | CUSTOM FABRICATION
234 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
235 | - | SPARE NUMBER
236 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
237 | 2 | PORTION SCALE | 120 | 1 | 0.5
238 | 1 | FOOD BLENDER | 120 | 1 | 15
239 | - | SPARE NUMBER
240 | - | SPARE NUMBER
241 | 1 | FOOD PROCESSOR | 120 | 1 | 7
242 | 1 | VEGETABLE SLICER | 120 | 1 | 3
243 | 1 | FOOD SLICER | 120 | 1 | 4
244 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
245 | - | SPARE NUMBER
246 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
247 | 1 | PREPARATION TABLE | [15 empty] | CUSTOM FABRICATION MOBILE
248 | 1 | PREPARATION TABLE | [15 empty] | CUSTOM FABRICATION MOBILE
249 | - | SPARE NUMBER
250 | - | SPARE NUMBER
251 | 1 | BULK PREPARATION COUNTER WITH SINKS | 120 | 1 | 40 |  | (2)1/2" | (2)1/2" | 45 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
252 | 1 | DOUBLE OVERSHELF WITH UTENSIL RACK | [15 empty] | CUSTOM FABRICATION PART OF ITEM #251
253 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
254 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
255 | - | SPARE NUMBER
256 | - | SPARE NUMBER
257 | - | SPARE NUMBER
258 | 2 | UTILITY RACK | [15 empty] | MOBILE
259 | - | SPARE NUMBER
260 | - | SPARE NUMBER
261 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 4600 | 3680 |  |  |  | WITH MAKE-UP AIR
262 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #261 #331 #352
263 | 1 | DOUBLE COMBI OVEN | 480 | 3 | 53.8 |  | (2)3/4" |  |  | (2)2" | [7 empty] | MOBILE
264 | 1 | DOUBLE CONVECTION OVEN | 120 | 1 | 6 | [6 empty] | 110000 | [5 empty] | MOBILE
265 | - | SPARE NUMBER
266 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
267 | 1 | SPREADER CABINET | [15 empty] | MOBILE CUSTOM FABRICATION WITH TRASH CHUTE
268 | 1 | FRYER BATTERY | 120 | 1 | 7 | [6 empty] | 240000 | [5 empty] | MOBILE WITH FILTER
269 | - | SPARE NUMBER
270 | - | SPARE NUMBER
271 | 1 | 40 GALLON TILTING SKILLET | 120 | 1 | 5 |  | 1/2" | 1/2" | 15 |  |  | 144000 | [5 empty] | WITH FAUCET
272 | 1 | 40 GALLON TILTING KETTLE | 120 | 1 | 5 |  | 1/2" | 1/2" | 15 |  |  | 100000 | [5 empty] | WITH FAUCET
273 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
274 | 1 | SIX BURNER RANGE WITH OVEN | [9 empty] | 260000 | [5 empty] | MOBILE
275-300 | - | SPARE NUMBERS
PASTRY PREPARATION AREA
301 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
302 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
303 | 1 | PASTRY PREPARATION COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
304 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
305 | - | SPARE NUMBER
306 | 1 | BATCH ICE CREAM FREEZER | 208 | 1 | 38 | [9 empty] | 8000
307 | 1 | DIPPERWELL |  |  |  |  | 1/2" |  |  | 1-1/2"
308 | 1 | ICE CREAM DIPPING CABINET | 120 | 1 | 3.2 |  |  |  |  | 3/4" | [7 empty] | MOBILE
309 | - | SPARE NUMBER
310 | - | SPARE NUMBER
311 | 1 | PASTRY PREPARATION COUNTER WITH SINK | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
312 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
313 | 1 | MARBLE TOP | [15 empty] | CUSTOM FABRICATION PART OF ITEM #311
314 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #311
315 | - | SPARE NUMBER
316 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWER PART OF ITEM #311
317 | 1 | PASTA MACHINE | 208 | 1 | 10
318 | 2 | INGREDIENT BIN | [15 empty] | MOBILE
319 | - | SPARE NUMBER
320 | - | SPARE NUMBER
321 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
322 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
323 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
324 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
325-330 | - | SPARE NUMBERS
FINISH COOKLINE
331 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 3300 | 3000 |  |  |  | WITH MAKE-UP AIR
332 | 1 | REACH-IN FREEZER | 120 | 1 | 6 | [12 empty] | MOBILE
333 | 1 | FRYER BATTERY | 120 | 1 | 7 | [6 empty] | 240000 | [5 empty] | MOBILE WITH FILTER
334 | 1 | SPREADER CABINET | [15 empty] | MOBILE CUSTOM FABRICATION WITH TRASH CHUTE
335 | - | SPARE NUMBER
336 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
337 | 1 | GRIDDLE WITH REFRIGERATED BASE | 120 | 1 | 12.6 | [6 empty] | 105000 | [5 empty] | MOBILE
338 | 1 | SPREADER CABINET | [15 empty] | MOBILE CUSTOM FABRICATION WITH TRASH CHUTE
339 | - | SPARE NUMBER
340 | - | SPARE NUMBER
341 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
342 | 1 | MODULAR SIX BURNER RANGE | [9 empty] | 210000
343 | 2 | SALAMANDER | [9 empty] | 35000 | [5 empty] | WALL MOUNTED
344 | 1 | MODULAR SIX BURNER RANGE | [9 empty] | 210000
345 | - | SPARE NUMBER
346 | 1 | FILL FAUCET |  |  |  |  | 3/4" | 3/4" | 30
347 | 1 | REFRIGERATED EQUIPMENT STAND | 120 | 1 | 12.6 | [12 empty] | MOBILE
348 | 1 | SPREADER CABINET | [15 empty] | MOBILE CUSTOM FABRICATION WITH TRASH CHUTE
349 | - | SPARE NUMBER
350 | - | SPARE NUMBER
351 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
352 | 1 | CHARBROILER | [15 empty] | MOBILE
353 | 1 | SOLID FUEL EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 2400 | 1279 |  |  |  | WITH MAKE-UP AIR
354 | 1 | ASH COLLECTOR | [15 empty] | BY OS&E
355 | - | SPARE NUMBER
356 | 1 | STAINLESS STEEL WOOD STORAGE CABINET | [15 empty] | CUSTOM FABRICATION MOBILE
357 | - | SPARE NUMBER
358 | - | SPARE NUMBER
359 | - | SPARE NUMBER
360 | - | SPARE NUMBER
361 | 1 | CHEF'S COUNTER WITH SINK | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
362 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION
363 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
364 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #361
365 | - | SPARE NUMBER
366 | 1 | FOOD WARMER | 120 | 1 | 11.2
367 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #361
368 | 1 | DIPPERWELL |  |  |  |  | 1/2" |  |  | 1-1/2"
369 | - | SPARE NUMBER
370 | - | SPARE NUMBER
371 | 1 | DROP-IN HOT/COLD WELL | 208 | 1 | 5.3 |  |  |  |  | 1" | [7 empty] | 2 WELLS
372 | 1 | FOOD WARMER | 120 | 1 | 5.5
373 | 1 | DIPPERWELL |  |  |  |  | 1/2" |  |  | 1-1/2"
374 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #361
375 | - | SPARE NUMBER
376 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #361
377 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
378 | 1 | PLATE AND BOWL SHELF | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
379 | - | SPARE NUMBER
380 | - | SPARE NUMBER
381 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
382 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #361
383 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #361
384 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
385 | - | SPARE NUMBER
386 | 1 | HOOD CONTROL CABINET | 120 | 1 | 4 | [12 empty] | FOR ITEM #261 #331 #352
387 | - | SPARE NUMBER
388 | - | SPARE NUMBER
389 | - | SPARE NUMBER
390-400 | - | SPARE NUMBERS
SHUCK STATION
401 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.3 | [12 empty] | MOBILE WITH DOOR
402 | 1 | SHUCK STATION COUNTER WITH SINKS | 120 | 1 | 40 |  | (2)1/2" | (2)1/2" | 30 | (2)1-1/2" | [7 empty] | CUSTOM FABRICATION
403 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
404 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #402
405 | - | SPARE NUMBER
406 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
407 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #402
408 | 1 | KNIFE SANITIZER | 120 | 1 | 10 | [12 empty] | WALL MOUNTED
409 | - | SPARE NUMBER
410 | - | SPARE NUMBER
411 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #402
412 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
413 | 1 | REFRIGERATED SHUCKING BIN WITH RAIL | 120 | 1 | 20 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION PART OF ITEM #402
414 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #402
415 | - | SPARE NUMBER
416 | 1 | PICK UP LANDING | [15 empty] | CUSTOM FABRICATION PART OF ITEM #402
417 | - | SPARE NUMBER
418 | - | SPARE NUMBER
419 | - | SPARE NUMBER
420 | - | SPARE NUMBER
BEVERAGE STATION AREA
421 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 3.8 | [12 empty] | MOBILE
422 | 1 | BEVERAGE COUNTER | 120 | 1 | 40 | [12 empty] | CUSTOM FABRICATION
423 | 1 | GLASS FILLER STATION |  |  |  |  | 1/2" |  |  | 3/4"
424 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
425 | - | SPARE NUMBER
426 | 1 | HOT WATER DISPENSER | 208 | 1 | 12.9 |  | 3/8"
427 | 3 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
428 | 1 | SODA AND ICE DISPENSER | 120 | 1 | 20 |  |  |  |  | 3/4" | [7 empty] | BY VENDOR
429 | - | SPARE NUMBER
430 | - | SPARE NUMBER
431 | 1 | ICE MACHINE | 120 | 1 | 12.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 5000 |  |  | 400LBS. AIR-COOLED NUGGET ICE
432 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #431
433 | 1 | COFFEE BREWER | 208 | 1 | 19.7 |  | 3/8"
434 | - | SPARE NUMBER
435 | - | SPARE NUMBER
436 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #426 #433 #438
437 | 2 | ESPRESSO GRINDER | 120 | 1 | 2.9
438 | 1 | ESPRESSO MACHINE | 208 | 1 | 32 |  | 3/8" |  |  | 1" | [7 empty] | 2 GROUP
439 | - | SPARE NUMBER
440 | - | SPARE NUMBER
441 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
442 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
443 | - | SPARE NUMBER
444 | - | SPARE NUMBER
445-450 | - | SPARE NUMBERS
WAREWASHING AREA
451 | 1 | QUEEN MARY CART | [15 empty] | MOBILE
452 | 3 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #453
453 | 1 | SOILED DISH TABLE | [15 empty] | CUSTOM FABRICATION WITH TROUGH AND BRIDGES
454 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #453
455 | - | SPARE NUMBER
456 | 3 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
457 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
458 | 1 | HOSE REEL | [15 empty] | CEILING MOUNT
459 | - | SPARE NUMBER
460 | - | SPARE NUMBER
461 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
462 | 1 | FOOD WASTE COLLECTOR | 208 | 3 | 3.2 |  | 1/2" | 1/2" | 15 |  | 1/2" | [6 empty] | WITH COVER
463 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
464 | 1 | DISH MACHINE | 208 | 3 | 51 |  | (2)1/2" |  |  | 2" |  |  |  |  | 6100 |  |  | 180°F RINSE VENTLESS
465 | - | SPARE NUMBER
466 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
467 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
468 | 1 | UNDERCOUNTER DISH MACHINE | 208 | 1 | 24.2 |  |  | 3/4" | 20 | 3/4"
469 | - | SPARE NUMBER
470 | - | SPARE NUMBER
471 | 1 | UNDERCOUNTER DISH MACHINE | 208 | 1 | 24.2 |  |  | 3/4" | 20 | 3/4"
472 | 1 | HOSE REEL CONTROL CABINET |  |  |  |  | 1/2" | 1/2" | 25 | [8 empty] | FOR ITEM #458
473 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
474 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
475 | - | SPARE NUMBER
476 | 4 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED THREE TIER
477 | 1 | POT SINK |  |  |  |  | (2)3/4" | (2)3/4" | 90 | (3)2" | [7 empty] | CUSTOM FABRICATION
478 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
479 | - | SPARE NUMBER
480 | - | SPARE NUMBER
481 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
482 | 1 | HOSE REEL | [15 empty] | CEILING MOUNT
483 | 1 | HOSE REEL CONTROL CABINET |  |  |  |  | 1/2" | 1/2" | 25 | [8 empty] | FOR ITEM #482
484 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
485 | - | SPARE NUMBER
486 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
487 | 2 | POT AND PAN SHELVING | [15 empty] | MOBILE FOUR TIER
488 | 2 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
489 | - | SPARE NUMBER
490 | - | SPARE NUMBER
491 | 4 | DISH DOLLY
492 | 4 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
493 | 4 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED THREE TIER
494 | - | SPARE NUMBER
495-500 | - | SPARE NUMBERS
CATERING/BANQUET STAGING AREA
501 | 1 | ROLL-IN REFRIGERATOR | 120 | 1 | 11.8
502 | 2 | UTILITY RACK | [15 empty] | MOBILE
503 | 1 | ROLL-IN REFRIGERATOR | 120 | 1 | 11.8
504 | 2 | UTILITY RACK | [15 empty] | MOBILE
505 | - | SPARE NUMBER
506 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
507 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
508 | 1 | POT SINK |  |  |  |  | (2)3/4" | (2)3/4" | 90 | (3)2" | [7 empty] | CUSTOM FABRICATION
509 | - | SPARE NUMBER
510 | - | SPARE NUMBER
511 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
512 | 1 | MOP SINK CABINET |  |  |  |  | 1/2" | 1/2" | 30 |  | 2" | [6 empty] | WITH HOSE BIBB
513 | 4 | BANQUET HEATED CABINET | 120 | 1 | 10.8 | [12 empty] | MOBILE
514 | 1 | PLATING TABLE | [15 empty] | CUSTOM FABRICATION
515 | - | SPARE NUMBER
516 | 3 | DISH DOLLY
517 | - | SPARE NUMBER
518 | - | SPARE NUMBER
519 | - | SPARE NUMBER
520-530 | - | SPARE NUMBER
531 | 1 | QUEEN MARY CART | [15 empty] | MOBILE
532 | 1 | QUEEN MARY CART | [15 empty] | MOBILE
533 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #534
534 | 1 | ICE MACHINE | 208 | 1 | 23.3 |  | 3/8" |  |  | 3/4" |  |  |  |  | 5500 |  |  | 1900LBS. AIR-COOLED CUBE ICE
535 | - | SPARE NUMBER
536 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 1750LBS
537 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
538 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
539 | - | SPARE NUMBER
540 | - | SPARE NUMBER
541 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
542 | 2 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
543 | 1 | BEVERAGE COUNTER WITH GLASS FILL SINK | 120 | 1 | 20 |  |  |  |  | 1-1/2" | [7 empty] | CUSTOM FABRICATION
544 | 1 | GLASS FILLER FAUCET |  |  |  |  | 1/2"
545 | - | SPARE NUMBER
546 | 1 | ICED TEA BREWER | 120 | 1 | 18 |  | 3/8"
547 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #546 #548 #551
548 | 1 | HOT WATER DISPENSER | 208 | 1 | 12.9 |  | 3/8"
549 | - | SPARE NUMBER
550 | - | SPARE NUMBER
551 | 1 | COFFEE BREWER | 120 | 1 | 28.3 |  | 1/4" | [10 empty] | BY VENDOR
552 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 3.8 | [12 empty] | MOBILE
553 | 1 | QUEEN MARY CART | [15 empty] | MOBILE
554 | - | SPARE NUMBER
555-600 | - | SPARE NUMBERS
LOBBY BAR AREA
601 | 1 | BAR TOP AND DIE | [15 empty] | BY INTERIOR DESIGNER WITH DRINK RAIL GRANITE TOP
602 | 1 | DRINK RAIL | [15 empty] | BY INTERIOR DESIGNER PART OF ITEM #601
603 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
604 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
605 | - | SPARE NUMBER
606 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
607 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
608 | 1 | COCKTAIL STATION | [7 empty] | 1"
609 | - | SPARE NUMBER
610 | - | SPARE NUMBER
611 | 1 | DOUBLE SPEED RAIL
612 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
613 | 1 | SODA GUN HOLDER
614 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #613
615 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
616 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
617 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
618 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
619 | - | SPARE NUMBER
620 | - | SPARE NUMBER
621 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
622 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
623 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
624 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | [7 empty] | 180° RINSE
625 | - | SPARE NUMBER
626 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
627 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
628 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
629 | - | SPARE NUMBER
630 | - | SPARE NUMBER
631 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
632 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
633 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
634 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
635 | - | SPARE NUMBER
636 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
637 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
638 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
639 | - | SPARE NUMBER
640 | - | SPARE NUMBER
641 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
642 | 1 | COCKTAIL STATION | [7 empty] | 1"
643 | 1 | DOUBLE SPEED RAIL
644 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
645 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
646 | 1 | SODA GUN HOLDER
647 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #646
648 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
649 | - | SPARE NUMBER
650 | - | SPARE NUMBER
651 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
652 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
653 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
654 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
655 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
656 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
657 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
658 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
659 | - | SPARE NUMBER
660 | - | SPARE NUMBER
661 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
662 | 1 | COCKTAIL STATION | [7 empty] | 1"
663 | 1 | DOUBLE SPEED RAIL
664 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
665 | - | SPARE NUMBER
666 | 1 | SODA GUN HOLDER
667 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #666
668 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
669 | - | SPARE NUMBER
670 | - | SPARE NUMBER
671 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
672 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
673 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
674 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
675 | - | SPARE NUMBER
676 | 1 | DRAINBOARD
677 | 6 | TASK LIGHT | 120 | 1 | 0.2 | [12 empty] | BY INTERIOR DESIGNER
678 | 1 | FLIP TOP DOOR | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
679 | - | SPARE NUMBER
680 | - | SPARE NUMBER
681 | 1 | BACK BAR COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
682 | 1 | BEER DISPENSING TOWER | [15 empty] | 4 TAP
683 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
684 | - | SPARE NUMBER
685-700 | - | SPARE NUMBERS
MARKET AREA
701 | 1 | SERVING COUNTER WITH SINKS | 120 | 1 | 80 |  | 1/2" | 1/2" | 30 | [8 empty] | MILLWORK / BY GENERAL CONTRACTOR
702 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
703 | 2 | RAPID COOK OVEN | 208 | 1 | 40 | [12 empty] | VENTLESS
704 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE WITH DOORS
705 | - | SPARE NUMBER
706 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 6.4 | [12 empty] | MOBILE WITH DRAWERS
707 | 1 | PANINI GRILL | 120 | 1 | 13.3
708 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE WITH DOOR
709 | - | SPARE NUMBER
710 | - | SPARE NUMBER
711 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
712 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
713 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
714 | 1 | COFFEE BREWER | 208 | 1 | 25.4 |  | 3/8"
715 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #714 #722 #734
716 | 1 | COFFEE GRINDER | 120 | 1 | 7.2
717 | 1 | KNOCK BOX | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
718 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
719 | - | SPARE NUMBER
720 | - | SPARE NUMBER
721 | 1 | ICED TEA BREWER | 208 | 1 | 11.1 |  | 3/8"
722 | 1 | HOT WATER DISPENSER | 208 | 1 | 12.9 |  | 3/8"
723 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE WITH DOOR
724 | 1 | DROP-IN ICE BIN | [7 empty] | 1" | [7 empty] | 45 LBS.
725 | - | SPARE NUMBER
726 | 2 | BLENDER | 120 | 1 | 15 | [12 empty] | WITH DOME
727 | 1 | MILLWORK SURROUND | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
728 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
729 | - | SPARE NUMBER
730 | - | SPARE NUMBER
731 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
732 | 1 | CONDIMENT CADDY | [15 empty] | BY OS&E
733 | - | SPARE NUMBER
734 | 1 | ESPRESSO MACHINE | 208 | 1 | 32 |  | 3/8" |  |  | 1" | [7 empty] | BY VENDOR
735 | - | SPARE NUMBER
736 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE WITH DOOR
737 | 1 | ESPRESSO GRINDER | 120 | 1 | 4
738 | 1 | KNOCK BOX | [15 empty] | CUSTOM FABRICATION PART OF ITEM #701
739 | - | SPARE NUMBER
740 | - | SPARE NUMBER
741 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
742 | 2 | POS SYSTEM | 120 | 1 | 20 | [12 empty] | BY OS&E
743 | 2 | DISPOSABLE CUP DISPENSER | [15 empty] | BY OS&E
744 | 1 | REFRIGERATED/AMBIENT GRAB N GO CASE | 120 | 1 | 15.2 | [12 empty] | MOBILE
745 | - | SPARE NUMBER
746 | 1 | FLIP TOP DOOR | [15 empty] | CUSTOM FABRICATION
747 | 1 | REFRIGERATED GRAB-N-GO CASE | 208 | 1 | 11.9
748 | - | SPARE NUMBER
749 | - | SPARE NUMBER
750 | - | SPARE NUMBER
751 | 1 | ICE CART | [15 empty] | MOBILE 250LBS.
752 | - | SPARE NUMBER
753 | - | SPARE NUMBER
754 | - | SPARE NUMBER
755-800 | - | SPARE NUMBERS
BULK STORAGE AREA
801 | 2 | SODA SYSTEM AND RACK | 120 | 1 | 20 |  | 1/2" | [10 empty] | BY VENDOR
802 | 3 | CO2 TANK | [15 empty] | BY VENDOR
803 | 3 | BEVERAGE STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
804 | 1 | BEER SYSTEM SHELF | [15 empty] | WALL MOUNTED
805 | - | SPARE NUMBER
806 | 1 | BEER SYSTEM | 120 | 1 | 3.5 | [10 empty] | 3/8" | 3/8" | WATER-COOLED
807 | 5 | DRY STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
808 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 2576LBS.
809 | - | SPARE NUMBER
810 | - | SPARE NUMBER
811 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #812
812 | 1 | ICE MACHINE | 208 | 3 | 11.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 4000 | 3/8" | 1/2" | 1444LBS. WATER-COOLED CUBE ICE
813 | 1 | ICE MACHINE | 120 | 1 | 14.4 |  | 3/8" |  |  | 3/4" |  |  |  |  | 1000 | 3/8" | 1/2" | 500LBS. WATER-COOLED FLAKE ICE
814 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #813
816 | 2 | ICE CART | [15 empty] | MOBILE 250LBS.
817 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
818 | - | SPARE NUMBER
819 | - | SPARE NUMBER
820 | - | SPARE NUMBER
821 | 1 | CHEF'S COOLER | 120 | 1 | 20
822 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
823 | 1 | COOLER CONDENSING UNIT | 208 | 3 | 9.3 | [10 empty] | 1/2" | 1/2" | INDOOR WATER-COOLED ON EMERGENCY POWER
824 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
825 | - | SPARE NUMBER
826 | 7 | COOLER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
827 | 2 | KEG RACK
828 | 1 | DISPLAY COOLER SHELVING | [15 empty] | MOBILE
829 | - | SPARE NUMBERS
830 | - | SPARE NUMBER
831 | 1 | DISPLAY COOLER DOOR | 120 | 1 | 10
PREPARATION AND COOKING AREA
832 | 1 | COLD PREPARATION TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
833 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE WITH DOORS
834 | 1 | BLAST CHILLER/FREEZER | 120 | 1 | 9.3 |  |  |  |  | 1-1/4" | [7 empty] | MOBILE
835 | - | SPARE NUMBER
836 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #837
837 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 2333 | 1866 |  |  |  | WITH MAKE-UP AIR
838 | - | SPARE NUMBER
839 | - | SPARE NUMBER
840 | - | SPARE NUMBER
841 | 1 | FRYER BATTERY | 120 | 1 | 7 | [6 empty] | 240000 | [5 empty] | MOBILE WITH FILTER AND DUMP STATION
842 | 1 | SPREADER | [15 empty] | CUSTOM FABRICATION MOBILE WITH TRASH CHUTE
843 | 1 | STAINLESS STEEL TRASH RECEPTACLE | [15 empty] | CUSTOM FABRICATION
844 | 1 | GRIDDLE WITH REFRIGERATED BASE | 120 | 1 | 12.6 | [6 empty] | 105000 | [5 empty] | MOBILE
845 | - | SPARE NUMBER
846 | 1 | SIX BURNER RANGE WITH OVEN | [9 empty] | 245000 | [5 empty] | MOBILE
847 | 1 | FILL FAUCET |  |  |  |  | 3/4" | 3/4" | 30
848 | 1 | PICK-UP TABLE | [15 empty] | CUSTOM FABRICATION
849 | - | SPARE NUMBER
850 | - | SPARE NUMBER
851 |  | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #848
852 | 3 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
853 | 1 | SANDWICH/SALAD PREPARATION REFRIGERATOR | 120 | 1 | 6.5
854 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 6.4 | [12 empty] | MOBILE WITH DRAWERS
855 | - | SPARE NUMBER
856 | - | SPARE NUMBER
857 | 2 | FOOD WARMER | 120 | 1 | 7.9
858 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 4 | [12 empty] | MOBILE
859 | - | SPARE NUMBER
860 | - | SPARE NUMBER
861 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
862 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
863 | 1 | STONE HEARTH OVEN | 120 | 1 | 2 | [6 empty] | 55000 | [5 empty] | WITH EXHAUST HOOD
864 | 1 | PIZZA PREPARATION TABLE | [15 empty] | CUSTOM FABRICATION WITH MARBLE TOP
865 | - | SPARE NUMBER
866 | 1 | PIZZA PREPARATION REFRIGERATOR | 120 | 1 | 3.9 | [12 empty] | MOBILE WITH DRAWERS
867 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 3.8 | [12 empty] | MOBILE
868 | 1 | PICK-UP TABLE | [15 empty] | CUSTOM FABRICATION
869 | - | SPARE NUMBER
871 | 3 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #868
872 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 4 | [12 empty] | MOBILE
873 | 3 | HEAT LAMP | 120 | 1 | 3.1
874 | 1 | HOOD CONTROL CABINET | 120 | 1 | 4 | [12 empty] | FOR ITEM #837
875-880 | - | SPARE NUMBER
ICE CREAM AREA
881 | 1 | ICE CREAM SERVING TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
882 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
883 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #881
884 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
885 | - | SPARE NUMBER
886 | 1 | BATCH ICE CREAM FREEZER | 208 | 1 | 20 | [12 empty] | AIR-COOLED
887 | 1 | DIPPERWELL |  |  |  |  | 1/2" |  |  | 1-1/2"
888 | 1 | ICE CREAM DIPPING CABINET | 120 | 1 | 1.8
889 | - | SPARE NUMBER
890 | - | SPARE NUMBER
891 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #881
892 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
893 | 1 | POS SYSTEM | 120 | 1 | 20 | [12 empty] | BY OS&E
894 | 1 | POS PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
895 | - | SPARE NUMBER
896 | 1 | PASS THRU WINDOW WITH SHELF | [15 empty] | CUSTOM FABRICATION
897 | - | SPARE NUMBER
898 | - | SPARE NUMBER
899 | - | SPARE NUMBER
900 | - | SPARE NUMBER
WAREWASHING AREA
901 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
902 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
903 | 1 | SOILED DISH TABLE WITH SINK | [7 empty] | 2" | [7 empty] | CUSTOM FABRICATION
904 | 1 | DISH DROP WINDOW WITH SHELF | [15 empty] | CUSTOM FABRICATION
905 | - | SPARE NUMBER
906 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #903
907 | 2 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
908 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
909 | - | SPARE NUMBER
910 | - | SPARE NUMBER
911 | 1 | DISH MACHINE | 208 | 3 | 51 |  | (2)1/2" |  |  | 2" |  |  |  |  | 6100 |  |  | 180°F RINSE VENTLESS
912 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
913 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
914 | 1 | UNDERCOUNTER DISH MACHINE | 208 | 1 | 24.2 |  |  | 3/4" | 20 | 3/4"
915 | - | SPARE NUMBER
916 | 2 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
917 | 1 | POT SINK |  |  |  |  | 1/2' | 1/2" | 40 | (3)2" | [7 empty] | CUSTOM FABRICATION
918 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
919 | - | SPARE NUMBER
920 | - | SPARE NUMBER
921 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
922 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
923 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
924 | 1 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
925 | - | SPARE NUMBER
926 | 1 | MOP RACK | [15 empty] | BY GENERAL CONTRACTOR
927 | 1 | MOP SINK | [8 empty] | 2" | [6 empty] | BY GENERAL CONTRACTOR
928 | 1 | HOSE BIBB |  |  |  |  | 1/2" | 1/2" | [9 empty] | BY GENERAL CONTRACTOR
929 | - | SPARE NUMBER
930 | - | SPARE NUMBER
931 | 1 | WALL SHELF | [15 empty] | CUSTOM FABRICATION
932 | 2 | DETERGENT STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
933 | - | SPARE NUMBER
934 | - | SPARE NUMBER
935-1000 | - | SPARE NUMBERS
POOL BAR AREA
1001 | 1 | BAR TOP AND DIE | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1002 | 1 | DRINK RAIL | [15 empty] | BY INTERIOR DESIGNER PART OF ITEM #1001
1003 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1004 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1005 | - | SPARE NUMBER
1006 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1007 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | [7 empty] | 180° RINSE
1008 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2" | [7 empty] | CUSTOM DESIGN
1009 | - | SPARE NUMBER
1010 | - | SPARE NUMBER
1011 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1012 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1013 | 1 | COCKTAIL STATION | [7 empty] | 1"
1014 | 1 | DOUBLE SPEED RAIL
1015 | - | SPARE NUMBER
1016 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1017 | 1 | SODA GUN HOLDER
1018 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1017
1019 | - | SPARE NUMBER
1020 | - | SPARE NUMBER
1021 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1022 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1023 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1024 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1025 | - | SPARE NUMBER
1026 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1027 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1028 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1029 | - | SPARE NUMBER
1030 | - | SPARE NUMBER
1031 | 1 | COCKTAIL STATION | [7 empty] | 1"
1032 | 1 | DOUBLE SPEED RAIL
1033 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1034 | 1 | SODA GUN HOLDER
1035 | - | SPARE NUMBER
1036 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1034
1037 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1038 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1039 | - | SPARE NUMBER
1040 | - | SPARE NUMBER
1041 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1042 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" |  |  | 1-1/2"
1043 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1044 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
1045 | - | SPARE NUMBER
1046 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1047 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1048 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1049 | - | SPARE NUMBER
1050 | - | SPARE NUMBER
1051 | 1 | COCKTAIL STATION | [7 empty] | 1"
1052 | 1 | DOUBLE SPEED RAIL
1053 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1054 | 1 | SODA GUN HOLDER
1055 | - | SPARE NUMBER
1056 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1054
1057 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1058 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1059 | - | SPARE NUMBER
1060 | - | SPARE NUMBER
1061 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1062 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1063 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1064 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2"
1065 | - | SPARE NUMBER
1066 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1067 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1068 | 1 | COCKTAIL STATION | [7 empty] | 1"
1069 | - | SPARE NUMBER
1070 | - | SPARE NUMBER
1071 | 1 | DOUBLE SPEED RAIL
1072 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1073 | 1 | SODA GUN HOLDER
1074 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1073
1075 | - | SPARE NUMBER
1076 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1077 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1078 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1079 | - | SPARE NUMBER
1080 | - | SPARE NUMBER
1081 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1082 | - | SPARE NUMBER
1083 | - | SPARE NUMBER
1084 | - | SPARE NUMBER
1085 | - | SPARE NUMBER
1086 | 1 | BACK BAR COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1087 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 6.3 | [12 empty] | MOBILE
1088 | 1 | FROZEN DRINK MACHINE | 120 | 1 | 11
1089 | - | SPARE NUMBER
1090 | - | SPARE NUMBER
1091 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1092 | 1 | BEER DISPENSING TOWER | [15 empty] | 3 TAP
1093 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1094 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1095 | - | SPARE NUMBER
1096 | 1 | FROZEN DRINK MACHINE | 120 | 1 | 11
1097 | - | SPARE NUMBER
1098 | - | SPARE NUMBER
1099 | - | SPARE NUMBER
1100 | - | SPARE NUMBER
1101 | 1 | BACK BAR COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1102 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1103 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1104 | 1 | BEER DISPENSING TOWER | [15 empty] | 3 TAP
1105 | - | SPARE NUMBER
1106 | 1 | FROZEN DRINK MACHINE | 120 | 1 | 11
1107 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1108 | 1 | BAR TOP AND DIE | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1109 | - | SPARE NUMBER
1110 | 1 | DRINK RAIL | [15 empty] | BY INTERIOR DESIGNER PART OF ITEM #1108
1111 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1112 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1113 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2" | [7 empty] | CUSTOM DESIGN
1114 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1115 | - | SPARE NUMBER
1116 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1117 | 1 | COCKTAIL STATION | [7 empty] | 1"
1118 | 1 | DOUBLE SPEED RAIL
1119 | - | SPARE NUMBER
1120 | - | SPARE NUMBER
1121 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1122 | 1 | SODA GUN HOLDER
1123 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1122
1124 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1125 | - | SPARE NUMBER
1126 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1127 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1128 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1129 | - | SPARE NUMBER
1130 | - | SPARE NUMBER
1131 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1132 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | [7 empty] | 180° RINSE
1133 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1134 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
1135 | - | SPARE NUMBER
1136 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1137 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" |  |  | 1-1/2"
1138 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1139 | - | SPARE NUMBER
1140 | - | SPARE NUMBER
1141 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1142 | 1 | COCKTAIL STATION | [7 empty] | 1"
1143 | 1 | DOUBLE SPEED RAIL
1144 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1145 | - | SPARE NUMBER
1146 | 1 | SODA GUN HOLDER
1147 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1146
1148 | 1 | FILLER PIECE | [15 empty] | CUSTOM DESIGN
1149 | - | SPARE NUMBER
1150 | - | SPARE NUMBER
1151 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1152 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1153 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2"
1154 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1155 | - | SPARE NUMBER
1156 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1157 | 1 | BACK BAR COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1158 | 1 | FROZEN DRINK MACHINE | 120 | 1 | 11
1159 | - | SPARE NUMBER
1160 | - | SPARE NUMBER
1161 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 6.3 | [12 empty] | MOBILE
1162 | - | SPARE NUMBER
1163 | - | SPARE NUMBER
1164 | - | SPARE NUMBER
1165- 1200 | - | SPARE NUMBERS
BULK STORAGE AREA
1201 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 2576LBS.
1202 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" | [10 empty] | FOR ITEM #1203
1203 | 1 | ICE MACHINE | 208 | 3 | 11.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 4000 | 3/8" | 1/2" | 1444LBS. WATER-COOLED CUBE ICE
1204 | 1 | ICE MACHINE | 120 | 1 | 14.4 |  | 3/8" |  |  | 3/4" |  |  |  |  | 1000 | 3/8" | 1/2" | 500LBS. WATER-COOLED FLAKE ICE
1205 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
1206 | 2 | ICE CART | [15 empty] | MOBILE 250LBS.
1207 | 2 | SECURITY UNIT | [15 empty] | MOBILE
1208 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 5.9 | [12 empty] | MOBILE
1209 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #1204
1210 | - | SPARE NUMBER
1211 | 2 | CO2 TANK | [15 empty] | BY VENDOR
1212 | 1 | SODA SYSTEM AND RACK | 120 | 1 | 20 |  | 1/2" | [10 empty] | BY VENDOR
1213 | 4 | DRY STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
1214 | 1 | REACH-IN FREEZER | 120 | 1 | 9.4 | [12 empty] | MOBILE
1215 | 1 | COOLER CONDENSING UNIT | 208 | 3 | 4.7 | [10 empty] | 1/2" | 1/2" | INDOOR WATER-COOLED ON EMERGENCY POWER
1216 | 1 | BULK COOLER | 120 | 1 | 20
1217 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
1218 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
1219 | - | SPARE NUMBER
1220 | - | SPARE NUMBER
1221 | 5 | COOLER STORAGE SHELVING | [15 empty] | MOBILE FIVE TIER
1222 | 1 | KEG RACK
1223 | 1 | DRY STORAGE SHELVING | [15 empty] | FIXED FIVE TIER
1224 | 1 | BEER SYSTEM SHELF | [15 empty] | WALL MOUNTED
1225 | 1 | BEER SYSTEM | 120 | 1 | 3.5 | [10 empty] | 3/8" | 3/8" | WATER-COOLED
PREPARATION AREA
1226 | 1 | BACK PREPARATION COUNTER WITH SINK | 120 | 1 | 40 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
1227 | 1 | COUNTERTOP COMBI OVEN | 208 | 1 | 27.4 |  | 3/4" |  |  | 1-1/2" | [7 empty] | VENTLESS
1228 | 1 | RAPID COOK OVEN | 208 | 1 | 40 | [12 empty] | VENTLESS
1229 | - | SPARE NUMBER
1230 | - | SPARE NUMBER
1231 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS PART OF ITEM #1226
1232 | 1 | VENTLESS FRYER | 208 | 1 | 24
1233 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
1234 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DOORS AND NSF7 RAIL PART OF ITEM #1226
1235 | - | SPARE NUMBER
1236 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1226
1237 | 1 | PICK-UP COUNTER | 120 | 1 | 40 | [12 empty] | CUSTOM FABRICATION
1238 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
1239 | - | SPARE NUMBER
1240 | - | SPARE NUMBER
1241 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1237
1242 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
1243 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1237
1244 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #1237
1245 | - | SPARE NUMBER
1246 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1237
1247 | 1 | MICROWAVE OVEN | 120 | 1 | 9.6
1248 | 1 | FOOD WARMER | 120 | 1 | 5.5
1249 | - | SPARE NUMBER
1250 | - | SPARE NUMBER
1251 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION WITH DRAWERS AND NSF7 RAIL PART OF ITEM #1237
1252 | 1 | FOOD WARMER | 120 | 1 | 5.5
1253 | 1 | RECESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1237
1254 | - | SPARE NUMBER
1255 | - | SPARE NUMBER
WAREWASHING AREA
1256 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
1257 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
1258 | 1 | SOILED DISH TABLE WITH SINK | [7 empty] | 2" | [7 empty] | CUSTOM FABRICATION
1259 | - | SPARE NUMBER
1260 | - | SPARE NUMBER
1261 | 1 | DISH DROP WINDOW WITH SHELF | [15 empty] | CUSTOM FABRICATION
1262 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1258
1263 | 1 | SILVERWARE CHUTE | [15 empty] | CUSTOM FABRICATION
1264 | 1 | SILVER SOAK SINK | [15 empty] | MOBILE
1265 | - | SPARE NUMBER
1266 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
1267 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
1268 | 1 | DISH MACHINE | 208 | 3 | 45.4 |  | 1/2" | 1/2" | 30 | 1-1/2" |  |  |  |  | 4300 |  |  | 180°F RINSE VENTLESS
1269 | - | SPARE NUMBER
1270 | - | SPARE NUMBER
1271 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
1272 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION WALL MOUNTED
1273 | 1 | POT SINK |  |  |  |  | 3/4" | 3/4" | 40 | (3)2" | [7 empty] | CUSTOM FABRICATION
1274 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
1275 | - | SPARE NUMBER
1276 | 1 | PRE-RINSE UNIT |  |  |  |  | 1/2" | 1/2" | 50 | [8 empty] | WITH FAUCET
1277 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
1278 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
1279 | - | SPARE NUMBER
1280 | - | SPARE NUMBER
1281 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
1282 | 1 | POT AND PAN SHELVING | [15 empty] | MOBILE FOUR TIER
1283 | 1 | MOP SINK CABINET |  |  |  |  | 1/2" | 1/2" | 30 |  | 2" | [6 empty] | WITH HOSE BIBB
1284 | 1 | HOSE BIBB |  |  |  |  | 1/2" | 1/2" | [9 empty] | BY GENERAL CONTRACTOR
1285- 1300 | - | SPARE NUMBERS
SKY LOUNGE BAR
1301 | 1 | FLIP TOP DOOR | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1302 | 1 | BAR TOP AND DIE | [15 empty] | BY INTERIOR DESIGNER WITH DRINK RAIL GRANITE TOP
1303 | 1 | DRINK RAIL | [15 empty] | BY INTERIOR DESIGNER PART OF ITEM #1302
1304 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2" | [7 empty] | CUSTOM DESIGN
1305 | - | SPARE NUMBER
1306 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1307 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1308 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1309 | - | SPARE NUMBER
1310 | - | SPARE NUMBER
1311 | 1 | COCKTAIL STATION | [7 empty] | 1"
1312 | 1 | DOUBLE SPEED RAIL
1313 | 1 | SODA GUN HOLDER
1314 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1313
1315 | - | SPARE NUMBER
1316 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1317 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1318 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1319 | - | SPARE NUMBER
1320 | - | SPARE NUMBER
1321 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1322 | 1 | GLASSWASHER | 208 | 1 | 33 |  |  | 1/2" | 18 | 1" | [7 empty] | 180° RINSE
1323 | 1 | DRAINBOARD | [7 empty] | 1-1/2"
1324 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" |  |  | 1-1/2"
1325 | - | SPARE NUMBER
1326 | 1 | TRASH UNIT | [15 empty] | WITH SLIM JIM
1327 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2"
1328 | 1 | COCKTAIL STATION | [7 empty] | 1"
1329 | - | SPARE NUMBER
1330 | - | SPARE NUMBER
1331 | 1 | DOUBLE SPEED RAIL
1332 | 1 | SODA GUN HOLDER
1333 | 1 | SODA GUN | [15 empty] | BY VENDOR CONNECTED TO ITEM #1332
1334 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1335 | - | SPARE NUMBER
1336 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1337 | 1 | DRAINBOARD TOP | [15 empty] | CUSTOM DESIGN
1338 | 1 | CORNER DRAINBOARD | [7 empty] | 1-1/2" | [7 empty] | CUSTOM DESIGN
1339 | - | SPARE NUMBER
1340 | - | SPARE NUMBER
1341 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1342 | 1 | BACK BAR COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1343 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1344 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1345 | - | SPARE NUMBER
1346 | 1 | BEER DISPENSING TOWER | [15 empty] | 3 TAP
1347 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1348 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1349 | - | SPARE NUMBER
1350 | - | SPARE NUMBER
1351 | 1 | BACK BAR REFRIGERATOR | 120 | 1 | 5.5 | [12 empty] | MOBILE
1352 | 1 | BEER DISPENSING TOWER | [15 empty] | 3 TAP
1353 | 1 | DRIP TROUGH |  |  |  |  | 1/2" |  |  | 1/2" | [7 empty] | WITH RINSER
1354 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 1.6 | [12 empty] | MOBILE
1355 | - | SPARE NUMBER
1356 | 1 | UNDERCOUNTER FREEZER | 120 | 1 | 2.4 | [12 empty] | MOBILE WITH DRAWER
1357 | - | SPARE NUMBER
1358 | - | SPARE NUMBER
1359 | - | SPARE NUMBER
1360- 1400 | - | SPARE NUMBER
EMPLOYEE DINING AREA
1401 | 1 | SERVERY COUNTER | 120 | 1 | 40 | [12 empty] | CUSTOM FABRICATION
1402 | 1 | HOT FOOD WELL | 208 | 1 | 17.9 |  |  | 1/2" | 5 | 1" | [7 empty] | 3 WELLS AUTOFILL
1403 | 1 | FOOD WARMER | 120 | 1 | 7.9
1404 | 1 | SNEEZE GUARD | 120 | 1 | 5 | [12 empty] | CUSTOM DESIGN WITH LIGHTS
1405 | - | SPARE NUMBER
1406 | 1 | COLD FOOD WELL | 120 | 1 | 5.5 |  |  |  |  | 1" | [7 empty] | 3 WELLS
1407 | 1 | SNEEZE GUARD | 120 | 1 | 5 | [12 empty] | CUSTOM DESIGN WITH LIGHTS
1408 | 1 | REFRIGERATED GRAB-N-GO MERCHANDISER | 120 | 1 | 7
1409 | - | SPARE NUMBER
1410 | - | SPARE NUMBER
1411 | 3 | UTENSIL CROCK | [15 empty] | CUSTOM FABRICATION
1412 | 1 | TRAY RECESS | [15 empty] | CUSTOM FABRICATION
1413 | 2 | UTILITY RACK | [15 empty] | MOBILE
1414 | 1 | TRASH COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1415 | - | SPARE NUMBER
1416 | 2 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION PART OF ITEM #1414
1417 | 2 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
1418 | 1 | WALL CABINET | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
1419 | - | SPARE NUMBER
1420-1500 | - | SPARE NUMBERS
ICE AREA
1501 | 4 | ICE DISPENSER | 120 | 1 | 2 |  |  |  |  | 3/4"
1502 | 4 | ICE MACHINE | 120 | 1 | 11.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 1100 | 3/8" | 1/2" | 360LBS. WATER-COOLED CUBE STYLE
1503 | 4 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" | [10 empty] | FOR ITEM #1502
1504 | - | SPARE NUMBER
1505-1600 | - | SPARE NUMBERS
ICE AREA
1701 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" |  |  | 1/2" | [7 empty] | FOR ITEM #1702
1702 | 1 | ICE MACHINE | 208 | 1 | 23.3 |  | 3/8" |  |  | 3/4" |  |  |  |  | 5500 |  |  | 1900LBS. AIR-COOLED CUBE ICE
1703 | 1 | ICE BIN | [7 empty] | 1/2" | [7 empty] | 1020LBS.
1704 | - | SPARE NUMBER
1705- 1800 | - | SPARE NUMBERS
ICE AREA
1801 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" |  |  | 1/2" | [7 empty] | FOR ITEM #1802
1802 | 1 | ICE MACHINE | 208 | 1 | 23.3 |  | 3/8" |  |  | 3/4" |  |  |  |  | 5500 |  |  | 1900LBS. AIR-COOLED CUBE ICE
1803 | 1 | ICE BIN | [7 empty] | 1/2" | [7 empty] | 1020LBS.
1804 | - | SPARE NUMBER
1805 -1900 | - | SPARE NUMBERS
ICE AREA
1901 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" |  |  | 1/2" | [7 empty] | FOR ITEM #1902
1902 | 1 | ICE MACHINE | 208 | 1 | 23.3 |  | 3/8" |  |  | 3/4" |  |  |  |  | 5500 |  |  | 1900LBS. AIR-COOLED CUBE ICE
1903 | 1 | ICE BIN | [7 empty] | 1/2" | [7 empty] | 1020LBS.
1904 | - | SPARE NUMBER
1905- 2000 | - | SPARE NUMBERS
Total