## FS Utility Load Schedule
PRELIMINARY FOODSERVICE EQUIPMENT SCHEDULE
PROJECT NAME: PIEDMONT HENRY HOSPITAL | [17 empty] | Date: 02/19/2024
PROJECT NUMBER: 1223
ITEM | QTY | DESCRIPTION | VOLTS | PH | AMPS | KW | CW | HW | GPH | IW | DW | BTUS | EXH CFM | SUPPLY CFM | HEAT REJECTION | CHILLED WATER IN | CHILLED WATER OUT | REMARKS
BULK STORAGE AREA
1 | 1 | REFRIGERATION RACK | 480V 120 | 3 1 | 89.2 20.0 | [12 empty] | OUTDOOR, AIR-COOLED, ON EMERGENCY POWER
2 | - | SPARE NUMBER
3 | - | SPARE NUMBER
4 | - | SPARE NUMBER
5 | - | SPARE NUMBER
6 | - | SPARE NUMBER
7 | - | SPARE NUMBER
8 | - | SPARE NUMBER
9 | - | SPARE NUMBER
10 | - | SPARE NUMBER
11 | 1 | HIGH-DENSITY SHELVING
12 | 1 | HIGH-DENSITY SHELVING
13 | 2 | HIGH-DENSITY SHELVING
14 | 4 | DRY STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
15 | - | SPARE NUMBER
16 | 10 | NON-FOOD STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
17 | 9 | EQUIPMENT STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
18 | 1 | BEVERAGE COOLER | 120 | 1 | 20
19 | - | SPARE NUMBER
20 | - | SPARE NUMBER
21 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
22 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
23 | 5 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
24 | 6 | BEVERAGE STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
25 | - | SPARE NUMBER
26 | 2 | SODA BAG IN BOX RACK | 120 | 1 | 20 |  | 1/2" | [10 empty] | BY VENDOR
27 | 5 | CO2 TANK | [15 empty] | BY VENDOR
28 | 1 | AIR CURTAIN | 120 | 1 | 5.7 | [12 empty] | WALL MOUNTED, WITH UV, HEPAC AND IONIZER
29 | - | SPARE NUMBER
30 | - | SPARE NUMBER
31 | 1 | BULK COOLER | 120 120 | 1 1 | 20.0 20.0
32 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
33 | 2 | LOW-PROFILE EVAPORATOR COIL | 120 | 1 | 1.7 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
34 | 13 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
35 | - | SPARE NUMBER
36 | 1 | BULK FREEZER | 120 120 | 1 1 | 20.0 20.0
37 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
38 | 2 | EVAPORATOR COIL | 208 | 1 | 9.1 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
39 | - | SPARE NUMBER
40 | - | SPARE NUMBER
41 | 14 | FREEZER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
42 | 1 | THAW COOLER | 120 | 1 | 20
43 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
44 | 1 | EVAPORATOR COIL | 208 | 1 | 13.7 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
45 | - | SPARE NUMBER
46 | 8 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
47 | 2 | UTILITY RACK | [15 empty] | MOBILE
48 | 1 | DAIRY COOLER | 120 | 1 | 20
49 | - | SPARE NUMBER
50 | - | SPARE NUMBER
51 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
52 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
53 | 6 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
54 | - | SPARE NUMBER
55 | - | SPARE NUMBER
PREPARATION AREA
56 | 1 | PROTEIN FREEZER | 120 | 1 | 20
57 | 1 | EVAPORATOR COIL | 208 | 1 | 9.1 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
58 | 6 | FREEZER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
59 | - | SPARE NUMBER
60 | - | SPARE NUMBER
61 | 1 | PROTEIN COOLER | 120 | 1 | 20
62 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
63 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
64 | 8 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
65 | - | SPARE NUMBER
66 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
67 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
68 | - | SPARE NUMBER
69 | - | SPARE NUMBER
70 | - | SPARE NUMBER
71 | 1 | PREPARATION TABLE | 120 | 1 | (3)20.0 | [12 empty] | CUSTOM FABRICATION
72 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
73 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
74 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #91
75 | - | SPARE NUMBER
76 | 1 | MEAT GRINDER | 120 | 1 | 8
77 | 1 | VACUUM PACKAGING MACHINE | 120 | 1 | 20 | [12 empty] | MOBILE, WITH CART
78 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
79 | - | SPARE NUMBER
80 | - | SPARE NUMBER
81 | 2 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #71
82 | 1 | KNIFE SANITIZER | 120 | 1 | 10 | [12 empty] | WALL MOUNTED
83 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
84 | 2 | PORTION SCALE | 120 | 1 | 0.5
85 | - | SPARE NUMBER
86 | 1 | 20 QT. MIXER | 120 | 1 | 6
87 | 1 | MIXER UTENSIL RACK | [15 empty] | CUSTOM FABRICATION
88 | 1 | AIR PURIFIER | 120 | 1 | 0.8 | [12 empty] | WALL MOUNTED
89 | - | SPARE NUMBER
90 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
91 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (3)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
92 | 3 | UTILITY RACK | [15 empty] | MOBILE
93 | 2 | DRY STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
94 | 1 | LOW-PROFILE EVAPORATOR COIL | 120 | 1 | 1.7 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
95-100 | - | SPARE NUMBER
PREPARATION AREA
101 | 1 | VEGETABLE COOLER | 120 120 | 1 1 | 20.0 20.0
102 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
103 | 2 | LOW-PROFILE EVAPORATOR COIL | 120 | 1 | 0.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
104 | 11 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
105 | - | SPARE NUMBER
106 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
107 | 1 | PREPARATION TABLE WITH SINKS | 120 | 1 | (3)20.0 |  | 1/2" | 1/2" | 30 | 1-1/2" | [7 empty] | CUSTOM FABRICATION, WITH MIXER RECESS
108 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
109 | - | SPARE NUMBER
110 | - | SPARE NUMBER
111 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
112 | 1 | VEGETABLE DRYER | 120 | 1 | 2.5 | [12 empty] | MOBILE
113 | 2 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #107
114 | 1 | KNIFE SANITIZER | 120 | 1 | 10 | [12 empty] | WALL MOUNTED
115 | - | SPARE NUMBER
116 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
117 | 2 | PORTION SCALE | 120 | 1 | 0.5
118 | - | SPARE NUMBER
119 | - | SPARE NUMBER
120 | - | SPARE NUMBER
121 | 1 | 20 QT. MIXER | 120 | 1 | 6
122 | 1 | MIXER UTENSIL RACK | [15 empty] | CUSTOM FABRICATION
123 | - | SPARE NUMBER
124 | - | SPARE NUMBER
125 | - | SPARE NUMBER
126 | 1 | LOW-PROFILE EVAPORATOR COIL | 120 | 1 | 1.7 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
127 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
128 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
129 | - | SPARE NUMBER
130 | - | SPARE NUMBER
131 | 1 | FOOD PROCESSOR | 120 | 1 | 7
132 | 1 | VEGETABLE SLICER | 120 | 1 | 3
133 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
134 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
135 | - | SPARE NUMBER
136 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
137 | 1 | AIR PURIFIER | 120 | 1 | 0.8 | [12 empty] | WALL MOUNTED
138 | 2 | UTILITY RACK | [15 empty] | MOBILE
139 | - | SPARE NUMBER
140-145 | - | SPARE NUMBER
146 | 1 | CATERING COOLER | 120 | 1 | 20
147 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
148 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
149 | - | SPARE NUMBER
150 | - | SPARE NUMBER
151 | 6 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
152 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
153 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
154 | 2 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #152
155 | - | SPARE NUMBER
156 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
157 | 2 | PORTION SCALE | 120 | 1 | 0.5
158 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
159 | - | SPARE NUMBER
160 | - | SPARE NUMBER
161 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 5.9 | [12 empty] | MOBILE
162 | 3 | UTILITY RACK | [15 empty] | MOBILE
163 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
164 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
165 | - | SPARE NUMBER
166 | 1 | AIR PURIFIER | 120 | 1 | 0.8 | [12 empty] | WALL MOUNTED
167 | 1 | PREPARATION TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
168 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
169 | - | SPARE NUMBER
170 | - | SPARE NUMBER
171 | 1 | FOOD PROCESSOR | 120 | 1 | 7
172 | 1 | VEGETABLE SLICER | 120 | 1 | 3
173 | - | SPARE NUMBER
174 | - | SPARE NUMBER
175-180 | - | SPARE NUMBER
181 | - | SPARE NUMBER
182 | - | SPARE NUMBER
183 | - | SPARE NUMBER
184 | - | SPARE NUMBER
185 | - | SPARE NUMBER
186 | - | SPARE NUMBER
187 | - | SPARE NUMBER
188 | - | SPARE NUMBER
189 | - | SPARE NUMBER
190 | - | SPARE NUMBER
191 | 1 | FINISH COOLER | 120 120 | 1 1 | 20.0 20.0
192 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
193 | 2 | LOW-PROFILE EVAPORATOR COIL | 120 | 1 | 1.7 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
194 | 8 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
195 | - | SPARE NUMBER
196 | 7 | UTILITY RACK | [15 empty] | MOBILE
197 | 1 | BLAST CHILLER | 120 | 1 | 20
198 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
199 | - | SPARE NUMBER
200 | - | SPARE NUMBER
201 | 1 | BLAST CHILLER EVAPORATOR COIL | 208 | 1 | 20.2
202 | - | SPARE NUMBER
203 | - | SPARE NUMBER
204 | - | SPARE NUMBER
205 | - | SPARE NUMBER
206 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
207 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
208 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
209 | - | SPARE NUMBER
210 | - | SPARE NUMBER
211 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #206
212 | 1 | FOOD BLENDER | 120 | 1 | 15
213 | 1 | FOOD BLENDER | 120 | 1 | 15
214 | 1 | FOOD BLENDER | 120 | 1 | 15
215 | - | SPARE NUMBER
216 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 3.8 | [12 empty] | MOBILE
217 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
218 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
219 | - | SPARE NUMBER
220-225 | - | SPARE NUMBER
POT/PAN WASH AREA
226 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
227 | 3 | POT AND PAN DRYING RACK | [15 empty] | MOBILE, FOUR TIER
228 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
229 | - | SPARE NUMBER
230 | - | SPARE NUMBER
231 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION, WALL MOUNTED
232 | 1 | POT AND PAN WASHER | 480V | 3 | 40 |  | 1/2" | 3/4" |  | 1-1/2" | [7 empty] | 180°F RINSE
233 | 1 | CONDENSATE HOOD | [7 empty] | 1/2" |  |  | 600 |  |  |  |  | CUSTOM FABRICATION
234 | 1 | POT SINK |  |  |  |  | (2)3/4" | (2)3/4" | 90 | (3)2" | [7 empty] | CUSTOM FABRICATION
235 | - | SPARE NUMBER
236 | 1 | POT SHELF | [15 empty] | CUSTOM FABRICATION
237 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
238 | 1 | HOSE REEL | [15 empty] | CEILING MOUNT
239 | - | SPARE NUMBER
240 | - | SPARE NUMBER
241 | 1 | HOSE REEL CONTROL CABINET |  |  |  |  | 1/2" | 1/2" | 25 | [8 empty] | FOR ITEM #238
242 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
243 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
244 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
245-300 | - | SPARE NUMBER
ICE PRODUCTION AREA
301 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
302 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  |  | 1/2" | [7 empty] | FOR ITEM #304
303 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/4" |  |  | 1/2" | [7 empty] | FOR ITEM #307
304 | 1 | ICE MACHINE | 208 | 1 | 8.9 |  | 3/8" |  |  | 3/4" |  |  |  |  | 1500 | 3/8" | 3/8" | 800LB., WATER-COOLED, FLAKE ICE
305 | - | SPARE NUMBER
306 | 1 | ICE BIN | [7 empty] | 1" | [7 empty] | 1700LBS., WITH DIVIDER
307 | 1 | ICE MACHINE | 208 | 1 | 16 |  | 3/8" |  |  | 3/4" |  |  |  |  | 10,00 | 3/8" | 3/8" | 1400LB., WATER-COOLED, CUBE ICE
308 | 3 | ICE CART | [15 empty] | MOBILE, 250LBS.
309 | - | SPARE NUMBER
310-315 | - | SPARE NUMBER
BULK PREPARATION AREA
316 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
317 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
318 | 1 | PREPARATION TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
319 | - | SPARE NUMBER
320 | - | SPARE NUMBER
321 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
322 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
323 | 1 | 20 QT. MIXER | 120 | 1 | 6
324 | 1 | FOOD PROCESSOR | 120 | 1 | 7
325 | 1 | MIXER UTENSIL RACK | [15 empty] | CUSTOM FABRICATION
326 | 1 | UTILITY RACK | [15 empty] | MOBILE
327 | 1 | MOBILE PREPARATION TABLE | [15 empty] | CUSTOM FABRICATION
328 | 1 | POT AND PAN DRYING RACK | [15 empty] | MOBILE, FOUR TIER
329 | - | SPARE NUMBER
330 | - | SPARE NUMBER
331 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (4)20.0 |  | (2)1/2" | (2)1/2" | 45 | (3)1-1/2" | [7 empty] | CUSTOM FABRICATION
332 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
333 | 3 | INGREDIENT BIN | [15 empty] | MOBILE
334 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
335 | - | SPARE NUMBER
336 | 1 | 5 QT. MIXER | 120 | 1 | 4
337 | 1 | FOOD BLENDER | 120 | 1 | 15
338 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
339 | - | SPARE NUMBER
340 | - | SPARE NUMBER
341 | 2 | PORTION SCALE | 120 | 1 | 0.5
342 | 1 | FILLER FAUCET |  |  |  |  | 1/2" | 1/2" | 10
343 | 1 | 60 QT. MIXER | 208 | 3 | 10
344 | 1 | MIXER UTENSIL RACK | [15 empty] | CUSTOM FABRICATION
345 | - | SPARE NUMBER
346 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
347 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
348 | - | SPARE NUMBER
349 | - | SPARE NUMBER
350-355 | - | SPARE NUMBER
BULK COOKING AREA
356 | 1 | PREPARATION TABLE WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
357 | 1 | OVERSHELF WITH UTENSIL RACK | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #356
358 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
359 | - | SPARE NUMBER
360 | - | SPARE NUMBER
361 | 4 | UTILITY RACK | [15 empty] | MOBILE
362 | 1 | PREPARATION TABLE | 120 | 1 | (2)20.0 | [12 empty] | CUSTOM FABRICATION
363 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #362
364 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
365 | 2 | DRY STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
366 | 1 | HOOD CONTROL CABINET | 120 | 1 | 1 | [12 empty] | FOR ITEM #368 & #391
367 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #368
368 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 3087 2499 | 926EA 750EA |  |  |  | WITH MAKE-UP AIR
369 | - | SPARE NUMBER
370 | - | SPARE NUMBER
371 | 1 | DOUBLE CONVECTION OVEN | 120 120 | 1 1 | 6.0 6.0 | [6 empty] | 110000 | [5 empty] | MOBILE
372 | 1 | DOUBLE CONVECTION OVEN | 120 120 | 1 1 | 6.0 6.0 | [6 empty] | 110000 | [5 empty] | MOBILE
373 | 1 | CONVECTION STEAMER | 120 120 | 1 1 | 4.0 4.0 |  | (2)3/4" |  |  | 1-1/2" |  | (2)32,000 | [5 empty] | MOBILE, WITH STAND
374 | 1 | CONVECTION STEAMER | 120 120 | 1 1 | 4.0 4.0 |  | (2)3/4" |  |  | 1-1/2" |  | (2)32,000 | [5 empty] | MOBILE, WITH STAND
375 | - | SPARE NUMBER
376 | 1 | 4-BURNER RANGE | [9 empty] | 180000 | [5 empty] | W/ OVEN, MOBILE
377 | 1 | POT FILLER FAUCET |  |  |  |  | 3/4" | 3/4" | 30
378 | 1 | 40 GALLON TILTING KETTLE | 120 | 1 | 5 |  | 1/2" | 1/2" | 15 |  |  | 100000
379 | - | SPARE NUMBER
380 | - | SPARE NUMBER
381 | 1 | 40 GALLON TILTING SKILLET | 120 | 1 | 5 |  | 1/2" | 1/2" | 15 |  |  | 144000 | [5 empty] | WITH FAUCET
382 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
383 | 1 | PREPARATION TABLE | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
384 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION
385-390 | - | SPARE NUMBER
FINISH COOKING AREA
391 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 3525 2397 | 1058EA 719EA |  |  |  | WITH MAKE-UP AIR
392 | 1 | DOUBLE CONVECTION OVEN | 120 120 | 1 1 | 6.0 6.0 | [6 empty] | 110000 | [5 empty] | MOBILE
393 | 1 | CONVECTION STEAMER | 120 120 | 1 1 | 4.0 4.0 |  | (2)3/4" |  |  | 1-1/2" |  | (2)32,000 | [5 empty] | MOBILE, WITH STAND
394 | 1 | HOT TOP RANGE | [9 empty] | 120000 | [5 empty] | MOBILE, WITH OVEN
395 | - | SPARE NUMBER
396 | 1 | FRYER BATTERY | 120 120 | 1 1 | 6.8 7.3 | [6 empty] | 280000 | [5 empty] | MOBILE, WITH DUMP STATION
397 | 1 | SPREADER CABINET
398 | 1 | REFRIGERATED EQUIPMENT STAND | 120 | 1 | 3 | [12 empty] | MOBILE
399 | - | SPARE NUMBER
400 | - | SPARE NUMBER
401 | 1 | MODULAR SIX BURNER RANGE | [9 empty] | 24000
402 | 1 | POT FILLER FAUCET |  |  |  |  | 3/4" | 3/4" | 30
403 | 1 | MODULAR CHARBROILER | [9 empty] | 90000
404 | 1 | GRIDDLE | [9 empty] | 90000 | [5 empty] | MOBILE, WITH OVEN
405 | - | SPARE NUMBER
406 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #391
407 | 1 | WORK TABLE | [15 empty] | CUSTOM FABRICATION
408 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE
409 | - | SPARE NUMBER
410 | - | SPARE NUMBER
411 | 1 | RAPID COOK OVEN | 208 | 1 | 40 | [12 empty] | VENTLESS
412 | 1 | REACH-IN FREEZER | 120 | 1 | 6 | [12 empty] | MOBILE
413 | - | SPARE NUMBER
414 | - | SPARE NUMBER
415 | - | SPARE NUMBER
TRAY ASSEMBLY AREA
416 | 1 | PASS-THRU REFRIGERATOR | 120 | 1 | 4.8 | [12 empty] | MOBILE
417 | 1 | TRAY ASSEMBLY COUNTER WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
418 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
419 | - | SPARE NUMBER
420 | - | SPARE NUMBER
421 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #417
422 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
423 | 1 | INDUCTION BASE CHARGER | 208 | 1 | 15.9
424 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #417
425 | - | SPARE NUMBER
426 | 1 | PREPARATION LABEL PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
427 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DOORS AND NSF7 RAIL, PART OF ITEM#417
428 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #417
429 | - | SPARE NUMBER
430 | - | SPARE NUMBER
431 | 1 | MICROWAVE OVEN | 120 | 1 | 9.6
432 | 1 | HOT FOOD WELL | 208 | 1 | 17.9 |  | 1/2" |  |  | 1" | [7 empty] | 3 WELL, AUTOFILL
433 | 1 | FOOD WARMER | 208 | 1 | 13.7
434 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #417
435 | - | SPARE NUMBER
436 | 1 | PREPARATION LABEL PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
437 | 1 | TRAY MAKE-UP ROLLERS | [7 empty] | 1" | [7 empty] | CUSTOM FABRICATION, PART OF ITEM #417
438 | 1 | TRAY STARTER | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #417
439 | - | SPARE NUMBER
440 | - | SPARE NUMBER
441 | 1 | LOAD CENTER | 120/208 | 1 | 150 | [12 empty] | CUSTOM FABRICATION
442 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
443 | 1 | MOBILE PLATE AND DISH DISPENSER | 120 | 1 | 7.5 | [12 empty] | MOBILE, HEATED
444 | - | SPARE NUMBER
445 | - | SPARE NUMBER
446 | - | SPARE NUMBER
447 | 1 | TRAY ASSEMBLY COUNTER WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
448 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
449 | - | SPARE NUMBER
450 | - | SPARE NUMBER
451 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #447
452 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
453 | 1 | INDUCTION BASE CHARGER | 208 | 1 | 15.9
454 | 1 | DOUBLE OVERSHELF | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #447
455 | - | SPARE NUMBER
456 | 1 | PREPARATION LABEL PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
457 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DOORS AND NSF7 RAIL, PART OF ITEM #447
458 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #447
459 | - | SPARE NUMBER
460 | - | SPARE NUMBER
461 | 1 | MICROWAVE OVEN | 120 | 1 | 9.6
462 | 1 | HOT FOOD WELL | 208 | 1 | 17.9 |  | 1/2" |  |  | 1" | [7 empty] | 3 WELL, AUTOFILL
463 | 1 | FOOD WARMER | 208 | 1 | 13.7
464 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #447
465 | - | SPARE NUMBER
466 | 1 | PREPARATION LABEL PRINTER | 120 | 1 | 5 | [12 empty] | BY OS&E
467 | 1 | TRAY MAKE-UP ROLLERS | [7 empty] | 1" | [7 empty] | CUSTOM FABRICATION, PART OF ITEM #447
468 | 1 | TRAY STARTER | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #447
469 | - | SPARE NUMBER
470 | - | SPARE NUMBER
471 | 1 | LOAD CENTER | 120/208 | 1 | 150 | [12 empty] | CUSTOM FABRICATION, PART OF ITEM #447
472 | 1 | PATIENT ROOM SCANNER | 120 | 1 | 5 | [12 empty] | BY OS&E
473 | 1 | MOBILE PLATE AND DISH DISPENSER | 120 | 1 | 7.5 | [12 empty] | MOBILE, HEATED
474 | 10 | MEAL TRAY DELIVERY CART | [15 empty] | MOBILE, PASS-THRU
475 | - | SPARE NUMBER
476 | 1 | AIR CURTAIN REFRIGERATOR | 120 | 1 | 8.3 | [12 empty] | MOBILE
477 | 1 | REACH-IN FREEZER | 120 | 1 | 6 | [12 empty] | MOBILE
478 | 1 | BEVERAGE COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
479 | - | SPARE NUMBER
480 | - | SPARE NUMBER
481 | 3 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
482 | 1 | COFFEE BREWER | 120/208 | 1 | 28.3 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
483 | 1 | JUICE DISPENSER | 120 | 1 | 6 |  | 3/8" | [10 empty] | BY VENDOR
484 | 1 | ICED TEA BREWER | 120 | 1 | 14.4 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
485 | - | SPARE NUMBER
486 | 1 | SODA AND ICE DISPENSER | 120 | 1 | 20 |  |  |  |  | 3/4" | [7 empty] | BY VENDOR
487 | 1 | ICE MACHINE | 120 | 1 | 15.2 |  | 3/8" |  |  | 3/4" |  |  |  |  | 7900 |  |  | 500LBS., AIR-COOLED
488 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  |  | 1/2" | [7 empty] | FOR ITEM #487
489 | - | SPARE NUMBER
490 | - | SPARE NUMBER
491 | 1 | AIR CURTAIN REFRIGERATOR | 120 | 1 | 8.3 | [12 empty] | MOBILE
492 | 1 | REACH-IN FREEZER | 120 | 1 | 6 | [12 empty] | MOBILE
493 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
494 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
495 | - | SPARE NUMBER
496 | 1 | DOME AND BASE STORAGE RACK | [15 empty] | MOBILE
497 | 1 | AIR CURTAIN | 120 | 1 | 11.4 | [12 empty] | WALL MOUNTED, WITH UV, HEPAC AND IONIZER
498 | - | SPARE NUMBER
499 | - | SPARE NUMBER
500 | - | SPARE NUMBER
JANITOR AREA
501 | 4 | DETERGENT STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
502 | 1 | MOP RACK | [15 empty] | BY GENERAL CONTRACTOR
503 | 1 | MOP SINK | [8 empty] | 2" | [6 empty] | BY GENERAL CONTRACTOR
504 | 1 | HOSE BIBB |  |  |  |  | 1/2" | 1/2" | [9 empty] | BY GENERAL CONTRACTOR
505 | - | SPARE NUMBER
506 | 1 | WALL SHELF | [15 empty] | CUSTOM FABRICATION
507 | 1 | AIR CURTAIN | 120 | 1 | 11.4 | [12 empty] | WALL MOUNTED, WITH UV, HEPAC AND IONIZER
508 | - | SPARE NUMBER
509 | - | SPARE NUMBER
510 | - | SPARE NUMBER
SOILED WARE WASHING AREA
511 | 1 | TRASH COOLER | 120 | 1 | 20
512 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
513 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
514 | 2 | TRASH TRUCK | [15 empty] | MOBILE
515 | - | SPARE NUMBER
516 | 11 | SOILED TRAY RETRIEVAL CART | [15 empty] | MOBILE
517 | 1 | SOILED DISH TABLE WITH TROUGH AND BRIDGE | [15 empty] | CUSTOM FABRICATION
518 | 1 | DOUBLE SIDED GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #517
519 | - | SPARE NUMBER
520 | - | SPARE NUMBER
521 | 1 | UTENSIL CHUTE | [15 empty] | CUSTOM FABRICATION
522 | 1 | SILVER SOAK SINK | [15 empty] | MOBILE
523 | 1 | TRASH RECEPTACLE | [15 empty] | WITH LID AND DOLLY
524 | 1 | FOOD WASTE COLLECTOR | 208 | 3 | 3.2 |  | 1/2" | 1/2" | 15 |  | 1/2" | [6 empty] | WITH COVER
525 | - | SPARE NUMBER
526 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION
527 | 1 | DISH MACHINE | 480V | 3 | 62 |  | (2)1/2" | 1/2" | 100 | 1-1/2" |  |  |  |  | 7200 |  |  | 180°F RINSE, VENTLESS
528 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
529 | - | SPARE NUMBER
530 | - | SPARE NUMBER
531 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
532 | 1 | EYE WASH STATION |  |  |  |  | 1/2" | 1/2" | 25 |  | 1-1/4"
533 | - | SPARE NUMBER
534 | - | SPARE NUMBER
535 | - | SPARE NUMBER
CLEAN WARE WASHING AREA
536 | 1 | PLASTIC DOOR
537 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
538 | 1 | HOSE STATION |  |  |  |  | 3/4" | 3/4" | 300 | 1/2" | [7 empty] | HOT & COLD WATER
539 | - | SPARE NUMBER
540 | - | SPARE NUMBER
541 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
542 | 1 | PLASTIC DOOR
543 | - | SPARE NUMBER
544 | - | SPARE NUMBER
545 | - | SPARE NUMBER
546 | 1 | EYE WASH STATION |  |  |  |  | 1/2" | 1/2" | 25 |  | 1-1/4"
547 | 1 | HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH VENDOR PROVIDED SOAP & TOWEL DISPENSER
548 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
549 | - | SPARE NUMBER
550 | - | SPARE NUMBER
551 | 1 | CLEAN DISH TABLE | [15 empty] | CUSTOM FABRICATION
552 | 1 | GLASS RACK SHELF | [15 empty] | CUSTOM FABRICATION, WALL MOUNTED
553 | 6 | CLEAN DISH STORAGE SHELVING | [15 empty] | FIXED, FIVE TIER
554 | 10 | GLASS RACK DISH DOLLY | [15 empty] | MOBILE
555 | - | SPARE NUMBER
556 | 10 | DISH DOLLY
557 | 6 | DOME AND BASE STORAGE RACK | [15 empty] | MOBILE
558 | 6 | TRAY DRYING/ STORAGE RACK | [15 empty] | MOBILE
559 | - | SPARE NUMBER
560 | - | SPARE NUMBER
561 | 6 | DOME AND BASE STORAGE RACK | [15 empty] | MOBILE
562 | - | SPARE NUMBER
563 | - | SPARE NUMBER
564 | - | SPARE NUMBER
565-600 | - | SPARE NUMBER
24HR GRAB-N-GO AREA
601 | 3 | REFRIGERATED GRAB-N-GO | 120 | 1 | 16 | [12 empty] | SELF CONTAINED
602 | 1 | REACH-IN FREEZER | 120 | 1 | 7.2 | [12 empty] | MOBILE, WITH GLASS DOOR
603 | 2 | REACH-IN REFRIGERATOR | 120 | 1 | 7.2 | [12 empty] | MOBILE, WITH GLASS DOOR
604 | 3 | AMBIENT GRAB-N-GO MERCHANDISER | 120 | 1 | 1.2
605 | - | SPARE NUMBER
606 | 1 | GRAB-N-GO COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
607 | 2 | SELF PAY POS SYSTEM | 120 | 1 | 10 | [12 empty] | BY VENDOR
608 | 1 | CONDIMENT DISPENSER | [15 empty] | BY OS&E
609 | - | SPARE NUMBER
610 | - | SPARE NUMBER
611 | 2 | MICROWAVE OVEN | 120 | 1 | 9.6
612 | 1 | GRAB-N-GO COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
613 | - | SPARE NUMBER
614 | - | SPARE NUMBER
615-650 | - | SPARE NUMBER
PHYSICIANS DINING AREA
651 | 1 | BEVERAGE COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
652 | 1 | ICE AND WATER DISPENSER | 120 | 1 | 9 |  | 3/8" |  |  | 3/4" | [7 empty] | BY VENDOR
653 | 1 | K-CUP COFFEE BREWER | 120 | 1 | 15 |  | 1/4" | [10 empty] | BY VENDOR
654 | 1 | JUICE DISPENSER | 120 | 1 | 6 |  | 3/8" | [10 empty] | BY VENDOR
655 | - | SPARE NUMBER
656 | 2 | MICROWAVE OVEN | 120 | 1 | 9.6
657 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE
658 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 6 | [12 empty] | MOBILE
659 | - | SPARE NUMBER
660-700 | - | SPARE NUMBER
SERVERY AREA
701 | 1 | TRAY/ SILVERWARE COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
702 | 1 | BEVERAGE COOLER | 120 | 1 | 20
703 | 1 | FLOOR TROUGH & GRATE | [8 empty] | 2" | [6 empty] | CUSTOM FABRICATION
704 | 1 | EVAPORATOR COIL | 120 | 1 | 1.8 |  |  |  |  | 3/4" | [7 empty] | ON EMERGENCY POWER
705 | - | SPARE NUMBER
706 | 3 | COOLER STORAGE SHELVING | [15 empty] | MOBILE, FIVE TIER
707 | 2 | DISPLAY COOLER SHELVING
708 | 2 | REACH-IN DOORS | 120 | 1 | 10
709 | - | SPARE NUMBER
710 | - | SPARE NUMBER
711 | 1 | BACK COUNTER WITH SINK | 120 | 1 | (2)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
712 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
713 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #711
714 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
715 | - | SPARE NUMBER
716 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
717 | 1 | FIRE SUPPRESSION SYSTEM | 120 | 1 | 20 | [12 empty] | FOR ITEM #718
718 | 1 | EXHAUST HOOD | 120 | 1 | 20 | [7 empty] | 3300 | 990EA |  |  |  | WITH MAKE-UP AIR
719 | 1 | HOOD CONTROL CABINET | 120 | 1 | 1 | [12 empty] | FOR ITEM #718
720 | - | SPARE NUMBER
721 | 1 | MODULAR GRIDDLE | [9 empty] | 90000
722 | 1 | REFRIGERATED EQUIPMENT STAND | 120 | 1 | 3 | [12 empty] | MOBILE
723 | 1 | MODULAR CHARBROILER | [9 empty] | 90000
724 | 1 | FRYER BATTERY | 120 120 | 1 1 | 6.8 7.3 | [6 empty] | 280000 | [5 empty] | MOBILE, WITH DUMP STATION
725 | - | SPARE NUMBER
726 | 1 | BACK COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
727 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
728 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
729 | - | SPARE NUMBER
730 | - | SPARE NUMBER
731 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #711
732 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
733 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 5.9 | [12 empty] | MOBILE, WITH GLASS DOORS
734 | - | SPARE NUMBER
735 | - | SPARE NUMBER
736 | 1 | GRILL SERVING COUNTER | [15 empty] | CUSTOM FABRICATION
737 | 1 | LOAD CENTER | 120/208 | 1 | 80 | [12 empty] | CUSTOM FABRICATION, PART OF ITEM #736
738 | 1 | BUTCHER BLOCK TOP | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #736
739 | - | SPARE NUMBER
740 | - | SPARE NUMBER
741 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
742 | 1 | FOOD WARMER | 120 | 1 | 1.1
743 | 1 | HOT FOOD WELL | 208 | 3 | 23.8 |  | 1/2" |  |  | 1" | [7 empty] | 4 WELLS, WITH AUTOFILL
744 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
745 | - | SPARE NUMBER
746 | 1 | FOOD WARMER | 120 | 1 | 1.1
747 | 1 | DROP-IN HOT FOOD WELL | 208 | 1 | 6 |  | 1/2" |  |  | 1/2" | [7 empty] | 2 WELLS, AUTOFILL
748 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
749 | - | SPARE NUMBER
750 | - | SPARE NUMBER
751 | 1 | FOOD WARMER | 120 | 1 | 6.7
752 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DRAWERS AND NSF7 RAIL, PART OF ITEM#736
753 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
754 | 1 | POS SYSTEM | 120 | 1 | 10 | [12 empty] | BY OS&E
755-765 | - | SPARE NUMBER
766 | 1 | PIZZA PREP TABLE | 120 | 1 | 3.9 | [12 empty] | MOBILE
767 | 1 | PIZZA OVEN | 120 | 1 | 2 | [6 empty] | 188000
768 | 1 | PIZZA OVEN EXHAUST HOOD | [10 empty] | 685
769 | - | SPARE NUMBER
770 | 1 | BACK COUNTER | 120 | 1 | (2)20.0 | [12 empty] | CUSTOM FABRICATION
771 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
772 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE
773 | 2 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #770
774 | - | SPARE NUMBER
775 | - | SPARE NUMBER
776 | 1 | PIZZA SERVING COUNTER | [15 empty] | CUSTOM FABRICATION
777 | 1 | LOAD CENTER | 120/208 | 1 | 80 | [12 empty] | CUSTOM FABRICATION, PART OF ITEM #776
778 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DRAWERS, PART OF ITEM#776
779 | - | SPARE NUMBER
780 | - | SPARE NUMBER
781 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #776
782 | 1 | DROP-IN HEATED SHELF | 120 | 1 | 9.2
783 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
784 | 1 | FOOD WARMER | 208 | 1 | 13.7
785 | - | SPARE NUMBER
786 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DRAWERS, PART OF ITEM#776
787 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #776
788 | 1 | DROP-IN HEATED SHELF | 120 | 1 | 9.2
789 | - | SPARE NUMBER
790 | - | SPARE NUMBER
791 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
792 | 1 | FOOD WARMER | 208 | 1 | 13.7
793 | - | SPARE NUMBER
794 | - | SPARE NUMBER
795-800 | - | SPARE NUMBER
801 | 1 | REACH-IN REFRIGERATOR | 120 | 1 | 6 | [12 empty] | MOBILE
802 | 1 | BACK COUNTER WITH SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
803 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #802
804 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
805 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
806 | 1 | BACK COUNTER | 120 | 1 | (2)20.0 | [12 empty] | CUSTOM FABRICATION
807 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE
808 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #802
809 | - | SPARE NUMBER
810 | - | SPARE NUMBER
811 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
812 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
813 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
814 | - | SPARE NUMBER
815 | - | SPARE NUMBER
816 | 1 | DELI SERVING COUNTER | [15 empty] | CUSTOM FABRICATION
817 | 1 | LOAD CENTER | 120/208 | 1 | 30 | [12 empty] | CUSTOM FABRICATION, PART OF ITEM #816
818 | 1 | GLASS SURROUND | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #816
819 | - | SPARE NUMBER
820 | - | SPARE NUMBER
821 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #816
822 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DRAWERS AND NSF7 RAIL, PART OF ITEM#816
823 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
824 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 8 |  |  |  |  | 1" | [7 empty] | CUSTOM FABRICATION, WITH DRAWERS AND NSF7 RAIL, PART OF ITEM#816
825 | - | SPARE NUMBER
826 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
827 | - | SPARE NUMBER
828 | - | SPARE NUMBER
829 | - | SPARE NUMBER
830 | - | SPARE NUMBER
831 | 1 | SALAD COUNTER | [15 empty] | CUSTOM FABRICATION
832 | 10 | SILVERWARE BIN | [15 empty] | BY OS&E
833 | 1 | HOT FOOD WELL | 120 | 1 | 13.8 |  | 1/2" |  |  | 1/2" | [7 empty] | 1 WELL, AUTOFILL
834 | 1 | REFRIGERATED COLD WELL | 120 | 1 | 2.8 |  |  |  |  | 1" | [7 empty] | 2 WELLS
835 | - | SPARE NUMBER
836 | 1 | DOUBLE SIDED SNEEZE GUARD | 120 | 1 | 5 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
837 | 1 | REFRIGERATED COLD WELL | 120 | 1 | 5.5 |  |  |  |  | 1" | [7 empty] | 3 WELLS
838 | 1 | DOUBLE SIDED SNEEZE GUARD | 120 | 1 | 5 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
839 | - | SPARE NUMBER
840 | - | SPARE NUMBER
841 | 1 | BARISTA COUNTER | [15 empty] | CUSTOM FABRICATION
842 | 1 | PASTRY DISPLAY CASE | 120 | 1 | 2 | [12 empty] | CUSTOM FABRICATION, WITH LED LIGHTS
843 | - | SPARE NUMBER
844 | 1 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 2 | [12 empty] | MOBILE
845 | - | SPARE NUMBER
846 | 1 | GLASS SURROUND | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #841
847 | 1 | SYRUP RACK | [15 empty] | BY OS&E
848 | 1 | ESPRESSO MACHINE | 208 | 1 | 30 |  | 3/8" |  |  | 1-1/2"
849 | - | SPARE NUMBER
850 | - | SPARE NUMBER
851 | 2 | CUP DISPENSER
852 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #841
853 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
854 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION, PART OF ITEM #841
855 | - | SPARE NUMBER
856 | 1 | PICK-UP | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #841
857 | 1 | CONDIMENT DISPENSER | [15 empty] | BY OS&E
858 | 1 | NAPKIN DISPENSER | [15 empty] | BY OS&E
859 | - | SPARE NUMBER
860 | - | SPARE NUMBER
861 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  |  | 1/2" | [7 empty] | FOR ITEM #848
862 | 1 | DUMP SINK |  |  |  |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION, PART OF ITEM #867
863 | 1 | DROP-IN ICE BIN | [7 empty] | 1" | [7 empty] | 23 LBS
864 | 1 | GLASS RINSER |  |  |  |  | 1/2" |  |  | 1/2"
865 | - | SPARE NUMBER
866 | 1 | BLENDER | 120 | 1 | 15 | [12 empty] | WITH DOME
867 | 1 | BACK COUNTER WITH SINK | 120 | 1 | (3)20.0 |  | 1/2" | 1/2" | 15 | 1-1/2" | [7 empty] | CUSTOM FABRICATION
868 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
869 | - | SPARE NUMBER
870 | - | SPARE NUMBER
871 | 2 | UNDERCOUNTER REFRIGERATOR | 120 | 1 | 3 | [12 empty] | MOBILE
872 | 1 | TRASH CHUTE | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #867
873 | 1 | TRASH RECEPTACLE | [15 empty] | SLIM JIM
874 | 1 | DROP-IN HAND SINK |  |  |  |  | 1/2" | 1/2" | 5 |  | 1-1/2" | [6 empty] | WITH SOAP & TOWEL DISPENSER
875 | - | SPARE NUMBER
876 | - | SPARE NUMBER
877 | - | SPARE NUMBER
878 | 1 | BACK COUNTER | 120 | 1 | 20 | [12 empty] | CUSTOM FABRICATION
879 | - | SPARE NUMBER
880 | - | SPARE NUMBER
881 | 1 | DOUBLE WALL SHELF | [15 empty] | CUSTOM FABRICATION, WITH CONCEALED BRACKETS
882 | 1 | HEATED HOLDING CABINET | 120 | 1 | 14.2 | [12 empty] | MOBILE
883 | 1 | INTERNATIONAL SERVING COUNTER | [15 empty] | CUSTOM FABRICATION
884 | 1 | LOAD CENTER | 120/208 | 1 | 45 | [12 empty] | CUSTOM FABRICATION, PART OF ITEM #883
885 | - | SPARE NUMBER
886 | 1 | RECCESSED CUTTING BOARD | [15 empty] | CUSTOM FABRICATION, PART OF ITEM #883
887 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
888 | 1 | DROP-IN HOT FOOD WELL | 208 | 1 | 6 |  | 1/2" |  |  | 1/2" | [7 empty] | 2 WELLS, AUTOFILL
889 | - | SPARE NUMBER
890 | - | SPARE NUMBER
891 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
892 | 1 | FOOD WARMER | 120 | 1 | 5.5
893 | 1 | HOT FOOD WELL | 208 | 1 | 17.9 |  | 1/2" |  |  | 1" | [7 empty] | 3 WELL, AUTOFILL
894 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
895 | - | SPARE NUMBER
896 | 1 | FOOD WARMER | 120 | 1 | 6.7
897 | 1 | REFRIGERATED COLD WELL | 120 | 1 | 2.8 |  |  |  |  | 1" | [7 empty] | 2 WELLS
898 | 1 | SNEEZE GUARD | 120 | 1 | 2 | [12 empty] | CUSTOM DESIGN, WITH LED LIGHT
899 | - | SPARE NUMBER
900 | - | SPARE NUMBER
901 | 1 | DISPLAY COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
902 | - | SPARE NUMBER
903 | - | SPARE NUMBER
904 | - | SPARE NUMBER
905-910 | - | SPARE NUMBER
DINING AREA
911 | 1 | BEVERAGE COUNTER | 120 | 1 | (2)20.0 | [12 empty] | CUSTOM FABRICATION
912 | 1 | SODA AND ICE DISPENSER | 120 | 1 | 20 |  |  |  |  | 3/4" | [7 empty] | BY VENDOR
913 | 1 | ICE MACHINE | 120 | 1 | 15.2 |  | 3/8" |  |  | 3/4" |  |  |  |  | 7900 |  |  | 500LBS., AIR-COOLED
914 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  |  | 1/2" | [7 empty] | FOR ITEM #913
915 | - | SPARE NUMBER
916 | 1 | COFFEE BREWER | 120/208 | 1 | 28.3 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
917 | 1 | JUICE DISPENSER | 120 | 1 | 6 |  | 3/8" |  | 5 | [8 empty] | BY VENDOR
918 | 1 | ICED TEA BREWER | 120 | 1 | 14.4 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
919 | - | SPARE NUMBER
920 | - | SPARE NUMBER
921 | 3 | CONDIMENT DISPENSER | [15 empty] | BY OS&E
922 | 3 | LID DISPENSER | [15 empty] | BY OS&E
923 | 3 | NAPKIN DISPENSER | [15 empty] | BY OS&E
924 | 1 | REFRIGERATED GRAB-N-GO | 120 | 1 | 16 | [12 empty] | SELF CONTAINED
925-930 | - | SPARE NUMBER
931 | 1 | BEVERAGE COUNTER | 120 | 1 | (2)20.0 | [12 empty] | CUSTOM FABRICATION
932 | 1 | SODA AND ICE DISPENSER | 120 | 1 | 20 |  |  |  |  | 3/4" | [7 empty] | BY VENDOR
933 | 1 | ICE MACHINE | 120 | 1 | 15.2 |  | 3/8" |  |  | 3/4" |  |  |  |  | 7900 |  |  | 500LBS., AIR-COOLED
934 | 1 | WATER FILTRATION SYSTEM |  |  |  |  | 3/8" |  |  | 1/2" | [7 empty] | FOR ITEM #933
935 | - | SPARE NUMBER
936 | 1 | COFFEE BREWER | 120/208 | 1 | 28.3 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
937 | 1 | JUICE DISPENSER | 120 | 1 | 6 |  | 3/8" |  | 5 | [8 empty] | BY VENDOR
938 | 1 | ICED TEA BREWER | 120 | 1 | 14.4 |  | 1/4" |  | 5 | [8 empty] | BY VENDOR
939 | - | SPARE NUMBER
940 | - | SPARE NUMBER
941 | 3 | CONDIMENT DISPENSER | [15 empty] | BY OS&E
942 | 3 | LID DISPENSER | [15 empty] | BY OS&E
943 | 3 | NAPKIN DISPENSER | [15 empty] | BY OS&E
944 | 1 | REFRIGERATED GRAB-N-GO | 120 | 1 | 16 | [12 empty] | SELF CONTAINED
945-950 | - | SPARE NUMBER
951 | 1 | POS STATION | [15 empty] | CUSTOM FABRICATION
952 | 1 | POS SYSTEM | 120 | 1 | 10 | [12 empty] | BY OS&E
953 | 1 | CHAIR | [15 empty] | BY OS&E
954 | 1 | POS STATION | [15 empty] | CUSTOM FABRICATION
955 | - | SPARE NUMBER
956 | 1 | POS SYSTEM | 120 | 1 | 10 | [12 empty] | BY OS&E
957 | 1 | CHAIR | [15 empty] | BY OS&E
958 | - | SPARE NUMBER
959 | - | SPARE NUMBER
960 | - | SPARE NUMBER
961 | 3 | SOILED TRAY RETRIEVAL CART | [15 empty] | MOBILE
962 | 1 | MICROWAVE COUNTER | [15 empty] | MILLWORK / BY GENERAL CONTRACTOR
963 | 3 | MICROWAVE OVEN | 120 | 1 | 9.6
964 | - | SPARE NUMBER
965-1000 | - | SPARE NUMBER
|  | TOTAL |  |  | 2424.9 |  |  |  | 1055 |  |  | 2006000 | 4585 | 0
1

## LE Utility Load Schedule
PRELIMINARY LAUNDRY EQUIPMENT SCHEDULE
PROJECT NAME: [NAME] | [19 empty] | Date: 01/01/2021
PROJECT NUMBER: ####
ITEM | QTY | DESCRIPTION | VOLTS | PH | AMPS | KW | CW | HW | GPH | IW | DW | BTUS | EXH CFM | SUPPLY CFM | HEAT REJECTION | STEAM IN | STEAM OUT | AIR | VACUUM | REMARKS
# | # | SAMPLE |  |  |  | 0 | [13 empty] | SAMPLE
|  | TOTAL |  |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0
1